## Conduit Schedule
POWER CONDUIT | [11 empty] | 11111111
SHEET | CONDUIT | SIZE | CONDUCTORS | SERVICE | AG MATERIAL | UG MATERIAL | FROM | TO | DUCTBANKS | NOTES
E-36 | P000 | N/A | BY UTILITY | N/A | PVC GRS | PVC 40 | UTILITY | MAIN TRANSFORMER |  | COORDINATE NUMBER OF CONDUITS AND SIZES WITH UTILITY
E-36 | P001A | 8 - 4" | 7 SETS OF (3 - 500 MCM W/ 3/0 NEUT AND 350 MCM GND) | 480VAC | PVC GRS | PVC 40 | MAIN TRANSFORMER | MAIN SES | DB-1 | ONE SPARE CONDUIT WITH PULLCORD
E-36 | P001B | 8 - 4" | 7 SETS OF (3 - 500 MCM W/ 3/0 NEUT AND 350 MCM GND) | 480VAC | PVC GRS | PVC 40 | MAIN SES | MAIN ATS | DB-2 | ONE SPARE CONDUIT WITH PULLCORD
E-36 | P002A | 6 - 3" | 6 SETS OF (3 - 400 MCM W/ 3/0 NEUT AND 350 MCM GND) | 480VAC | GRS | PVC 40 | MAIN ATS | MAIN GENERATOR | DB-3 | ONE SPARE CONDUIT WITH PULLCORD
E-36 | P002B | 1" | 2 #10 W/ #10 GND | 120VAC | PVC GRS | PVC 40 | LP-AB | MAIN GENERATOR CHARGER | DB-3 | SERVES GENERATOR CHARGER
|  |  | 3 #10 W/ #10 GND | 240VAC |  |  |  | MAIN GENERATOR HEATER |  | SERVERS GENERATOR HEATER
E-36 | P003 | 7 - 4" | 6 SETS OF (3 - 500 MCM W/ 3/0 NEUT AND 350 MCM GND) | 480VAC | GRS | PVC 40 | MAIN ATS | SWBD-1
E-39 | P006A | 1" | 3 #8 W/ #10 GND | 480VAC | GRS | PVC 40 | SWBD-AB1 | LP-AB TRANSFORMER
E-39 | P006B | 1.5" | 4 #3 W/ #8 GND | 120VAC | GRS | PVC 40 | LP-AB TRANSFORMER | LP-AB
E-39 | P007 | 3/4" | 2 #12 W/ #12 GND | 120VAC | GRS | PVC 40 | LP-AB | PLC-AB
E-36 | P010 | 2 -3" | 2 SETS OF 3 - 350 MCM W/ #1 GND | 480VAC | GRS | PVC 40 | SWBD-AB1 | MCC-AB2 |  | VIA WIRE TRENCH
E-38 | P015 | 3/4" | 2 #12 W/ #12 GND | 120VAC | GRS | PVC 40 | LP-AB | 31-H-1100
E-38 | P019 | 3/4" | 2 #12 W/ #12 GND | 120VAC | GRS | PVC 40 | LP-AB | 31-H-1110
E-37 | P016 | 3/4" | 2 #12 | 120VAC | GRS | PVC 40 | LP-AB | MCC-AB2 |  | SERVES MCC-AB2 LOW LEVEL RELAY SECTION
|  |  | 2 #12 |  |  |  |  | MCC-AB3 |  | SERVES MCC-AB3 LOW LEVEL RELAY SECTION
E-38 | P017A | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | SWBD-AB1 | DS-31-H-1100
E-38 | P017B | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | DS-31-H-1100 | 31-H-1100
E-38 | P018A | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | SWBD-AB1 | DS-31-H-1200
E-38 | P018B | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | DS-31-H-1200 | 31-H-1200
E-37 | P019 | 3/4" | 2 #12 W/ #12 GND | 120VAC | GRS | PVC 40 | LP-AB | 31-H-1210
E-38 | P020 | 2-3" | 2 SETS OF 3 - 350 MCM W/ #1 GND | 480VAC | GRS | PVC 40 | SWBD-AB1 | MCC-AB3
E-40 | P030 | 2-3" | 2 SETS OF 3 - 4/0 MCM W/ #2 GND | 480VAC | GRS | PVC 40 | SWBD-AB1 | MCC-AB1
E-40 | P040 | 2-3" | 2 SETS OF 3 - 350 MCM W/ #1 GND | 480VAC | GRS | PVC 40 | SWBD-AB1 | MCC-AB4
E-37 | P050 | 1.5" | 4 #3 W/ #8 GND | 480VAC | GRS | PVC 40 | SWBD-AB1 | DP-AB2
E-41 | P051 | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | DP-AB2 | P-VLT25 | DB-4 | SERVES EXISTING DIGESTED SLUDGE PUMP AND VALVES PANEL
E-41 | P052 | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SERVES EXISTING DIGESTED SLUDGE PUMP AND VALVES PANEL
E-41 | P053 | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT26 | P#19 | DB-30
E-41 | P054 | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P#19 | EXISTING DIGESTED SLUDGE PUMP AND VALVES PANEL | EXISTING
E-42 | P066 | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | LP-AB | P-VLT28 | DB-6
E-39 | P067 | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | P-VLT28 | FUEL TANK CONTROLLER | DB-7
E-37 | P71 | 1" | 2 #10 W/ #10 GND | 120VAC | PVC GRS | PVC 40 | LP-MCC3 | THICKENER AREA SITE LIGHTS | DB-25
E-39 | P082 | 1" | 3 #12 W/ #12 GND | 240VAC | PVC GRS | PVC 40 | LP-AB | SITE LIGHTING 1 |  | SERVES SITE LIGHTING - 3 LIGHTS
E-39 | P083 | 1" | 3 #12 W/ #12 GND | 240VAC | PVC GRS | PVC 40 | LP-AB | SITE LIGHTING 2 |  | SERVES SITE LIGHTING - 4 LIGHTS
E-41 | P105A | 2" | 4 1/0 W/ #6 GND | 480VAC | GRS | PVC 40 | DP-AB2 | DS-PSU-UV-1 TXFR | DB-5
E-41 | P105B | 2" | 4 1/0 W/ #6 GND | 480VAC | GRS | PVC 40 | DS-PSU-UV-1 TXFR | PSU-UV-1 TXFR
E-41 | P105C | BY MFG | BY MFG | BY MFG | GRS | PVC 40 | PSU-UV-1 TXFR | PSU-UV-1
E-41 | P106A | 2" | 4 1/0 W/ #6 GND | 480VAC | GRS | PVC 40 | DP-AB2 | DS-PSU-UV-2 TXFR | DB-5
E-41 | P106B | 2" | 4 1/0 W/ #6 GND | 480VAC | GRS | PVC 40 | DS-PSU-UV-2 TXFR | PSU-UV-2 TXFR
E-41 | P106C | BY MFG | BY MFG | BY MFG | GRS | PVC 40 | PSU-UV-2 TXFR | PSU-UV-2
E-41 | P107 | 3/4" | 2 #12 W/ #12 GND | 120VAC | GRS | PVC 40 | LP-UV-2 | MCP-UV
E-41 | P108A | 3/4" | 3 #10 W/ #10 GND | 480VAC | GRS | PVC 40 | DP-AB2 | LP-UV-2 TXFR | DB-5
E-41 | P108B | 3" | 4 3/0 W/ #6 GND | 120VAC | GRS | PVC 40 | LP-UV-22 TXFR | LP-UV-2
E-41 | P110 | 1.5" | 2 #12 W/ #12 GND | 120VAC | GRS | PVC 40 | LP-UV-2 | PLC-AB | DB-5 | FOR 44-H-1611 CONTROL
|  |  | 2 #12 W/ #12 GND | [6 empty] | FOR 44-H-1621 CONTROL
|  |  | 2 #12 W/ #12 GND | [6 empty] | FOR 44-H-1631 CONTROL
E-41 | P112A | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | SWBD-AB1 | P-VLT25 | DB-4 | SERVES EXISTING DIGESTER SUPERNATANT STATION
E-41 | P112B | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SERVES EXISTING DIGESTER SUPERNATANT STATION
E-41 | P112C | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT26 | V#19P | DB-30 | SERVES EXISTING DIGESTER SUPERNATANT STATION
E-42 | P112D | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | V#19P | EXISTING POWER VAULT | EXISTING | CONTRACTOR TO INTERCEPT EXISITNG WIRE ROUTE AND PULL NEW WIRE FROM SWBD-1 TO DIGESTER SUPERNATANT STATION
E-41 | P120 | 2" | 3 #6/ W #10 GND | 240VAC | PVC GRS | PVC 40 | LP-RWDP | P-VLT30 | DB-19 | CONTRACTOR TO PULL NEW WIRE THROUGH P-VLT30 UP THE HILL TO FINAL TERMINATION POINT REPLACING EXISTING WIRE
E-41 | P121 | 2" | 2 #10 W/ #10 GND | 120VAC | PVC GRS | PVC 40 | LP-RWDP | P-VLT30 | DB-19 | CONTRACTOR TO PULL NEW WIRE THROUGH P-VLT30 UP THE HILL TO FINAL TERMINATION POINT REPLACING EXISTING WIRE
E-41 | P122 | 1" | PULL CORD | 240VAC | PVC GRS | PVC 40 | LP-RWDP | P-VLT30 | DB-19
E-41 | P123 | 1" | PULL CORD | 240VAC | PVC GRS | PVC 40 | LP-RWDP | P-VLT30 | DB-19
E-37 | P200 | 1.5" | 3 #3 W/ #8 GND | 480VAC | PVC GRS | PVC 40 | MCC-3 | DP-MCC3
E-42 | P300 | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | EX CONTROL PANEL | PLC-PSP
E-42 | P400 | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | EX MCC | PLC-PRP
E-42 | P21-1000 | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | PLC-PSP | 21-LIT-1000
E-37 | P21-1200A | 2" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | MCC-3 | P-VLT1 | DB-10 | SERVES 21-ME-1200 (POWER, HOA, JSH, JSHH, DISCONNECT AUX); CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 5 #14 | CONTROL
|  |  | 3 #10 W/ #10 GND | 480VAC | [5 empty] | SERVES 22-P-1200; CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 3 #8 W/ #10 GND | [6 empty] | SERVES 22-P-2200; CONTRACTOR TO MATCH EXISTING WIRE SIZES
E-37 | P21-1200B | 2" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | P-VLT1 | JBOX-2 | EXISTING | SERVES 21-ME-1200 (POWER, HOA, JSH, JSHH, DISCONNECT AUX); CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 5 #14 | CONTROL
|  |  | 3 #10 W/ #10 GND | 480VAC | [5 empty] | SERVES 22-P-1200; CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 3 #8 W/ #10 GND | [6 empty] | SERVES 22-P-2200; CONTRACTOR TO MATCH EXISTING WIRE SIZES
E-37 | P21-1200C | 2" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | JBOX-2 | P-VLT4 | EXISTING | SERVES 21-ME-1200 (POWER, HOA, JSH, JSHH, DISCONNECT AUX); CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 5 #14 | CONTROL
|  |  | 3 #10 W/ #10 GND | 480VAC | [5 empty] | SERVES 22-P-1200; CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 3 #8 W/ #10 GND | [6 empty] | SERVES 22-P-2200; CONTRACTOR TO MATCH EXISTING WIRE SIZES
E-37 | P21-1200D | 2" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | P-VLT4 | JBOX-3 | EXISTING | SERVES 21-ME-1200 (POWER, HOA, JSH, JSHH, DISCONNECT AUX); CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 5 #14 | CONTROL
|  |  | 3 #10 W/ #10 GND | 480VAC | [5 empty] | SERVES 22-P-1200; CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 3 #8 W/ #10 GND | [6 empty] | SERVES 22-P-2200; CONTRACTOR TO MATCH EXISTING WIRE SIZES
E-37 | P21-1200E | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | JBOX-3 | DS-21-ME-1200 |  | CONTRACTOR TO PULL NEW WIRE TO DISCONNECT MATCHING EXISTING WIRE SIZES; RE-USE EXISTING CONDUIT (EXISTING CONDUIT PC-7)
|  |  | 5 #14 | CONTROL
E-37 | P21-1204A | 2" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | LP-MCC3 | P-VLT1 | DB-10 | SERVES 21-LIT-1101 (LIT-1), 21-LIT-1204B (LIT-4), 21-LIT-1304B (LIT-7), 21-LIT-1305B (LIT-8)
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 21-LIT-1204A (LIT-2), 21-LIT-1205A (LIT-3), 21-LIT-1304A (LIT-5), 21-LIT-1305A (LIT-6)
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 51-LIT-1101
|  |  | 2 #10 W/ #10 GND | [6 empty] | SERVES POSSIBLE L1, L2, L3, L4, L5, L6, L8, L9; POWER TO BE ROUTED THROUGH THE LIGHTING CONTROL PANEL (LCP-AB); CONTRACTOR TO DETERMINE WHICH LIGHTS ARE POWERED HERE
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 96-ME-1100 (EXISTING FLARE)
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 96-FIT-1000
|  |  | 2 #14 | CONTROL |  |  | PLC-MCC-3 |  |  | SERVES 96-ME-1100 (EXISTING FLARE)
E-37 | P21-1204B | 2" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | P-VLT1 | JBOX2 | EXISTING | SERVES 21-LIT-1101 (LIT-1), 21-LIT-1204B (LIT-4), 21-LIT-1304B (LIT-7), 21-LIT-1305B (LIT-8)
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 21-LIT-1204A (LIT-2), 21-LIT-1205A (LIT-3), 21-LIT-1304A (LIT-5), 21-LIT-1305A (LIT-6)
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 51-LIT-1101
|  |  | 2 #10 W/ #10 GND | [6 empty] | SERVES POSSIBLE L1, L2, L3, L4, L5, L6, L8, L9; POWER TO BE ROUTED THROUGH THE LIGHTING CONTROL PANEL (LCP-AB); CONTRACTOR TO DETERMINE WHICH LIGHTS ARE POWERED HERE
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 96-ME-1100 (EXISTING FLARE)
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 96-FIT-1000
|  |  | 2 #14 | CONTROL | [5 empty] | SERVES 96-ME-1100 (EXISTING FLARE)
E-37 | P21-1204C | 2" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | JBOX2 | P-VLT4 | EXISTING | SERVES 21-LIT-1101 (LIT-1), 21-LIT-1204B (LIT-4), 21-LIT-1304B (LIT-7), 21-LIT-1305B (LIT-8)
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 21-LIT-1204A (LIT-2), 21-LIT-1205A (LIT-3), 21-LIT-1304A (LIT-5), 21-LIT-1305A (LIT-6)
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 51-LIT-1101
|  |  | 2 #10 W/ #10 GND | [6 empty] | SERVES POSSIBLE L1, L2, L3, L4, L5, L6, L8, L9; POWER TO BE ROUTED THROUGH THE LIGHTING CONTROL PANEL (LCP-AB); CONTRACTOR TO DETERMINE WHICH LIGHTS ARE POWERED HERE
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 96-ME-1100 (EXISTING FLARE)
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 96-FIT-1000
|  |  | 2 #14 | CONTROL | [5 empty] | SERVES 96-ME-1100 (EXISTING FLARE) |  | 1111111111111
POWER CONDUIT | [11 empty] | 2222222222222
SHEET | CONDUIT | SIZE | CONDUCTORS | SERVICE | AG MATERIAL | UG MATERIAL | FROM | TO | DUCTBANKS | NOTES
E-37 | P21-1204D | 2" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | P-VLT4 | J-BOX4 | EXISTING | CONTRACTOR TO PULL NEW WIRE TO J-BOX4, INSTALL TERMINAL BLOCKS AND INTERCEPT EXISTING WIRE | SERVES 21-LIT-1101 (LIT-1), 21-LIT-1204B (LIT-4), 21-LIT-1304B (LIT-7), 21-LIT-1305B (LIT-8) (EXISTING CONDUIT A-6)
|  |  | 2 #12 W/ #12 GND | [7 empty] | SERVES 21-LIT-1204A (LIT-2), 21-LIT-1205A (LIT-3), 21-LIT-1304A (LIT-5), 21-LIT-1305A (LIT-6) (EXISTING CONDUIT A-6)
|  |  | 2 #12 W/ #12 GND | [7 empty] | SERVES POSSIBLE L1, L2, L3, L4, L5, L6, L8, L9 (EXISTING CONDUIT PC-31); CONTRACTOR TO DETERMINE WHICH LIGHTS ARE POWERED HERE
|  |  | 2 #10 W/ #10 GND | [6 empty] | SERVES 51-LIT-1101
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 96-ME-1100 (EXISTING FLARE)
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 96-FIT-1000
|  |  | 2 #14 | CONTROL | [5 empty] | SERVES 96-ME-1100 (EXISTING FLARE)
E-37 | P21-1204E | 2" | 2 #10 W/ #10 GND | 120VAC | PVC GRS | PVC 40 | J-BOX4 | P-VLT3 | EXISTING | SERVES 51-LIT-1101
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 96-ME-1100 (EXISTING FLARE)
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 96-FIT-1000
E-37 | P21-1204F | 2" | 2 #10 W/ #10 GND | 120VAC | PVC GRS | PVC 40 | P-VLT3 | P-VLT2 | EXISTING | SERVES 51-LIT-1101
E-37 | P21-1210A | 2" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | DP-MCC3 | P-VLT1 | DB-10 | SERVES 21-FCV-1210; CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 21-FCV-1310; CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 21-FCV-1410; CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 22-FCV-2301; CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 22-FCV-2302; CONTRACTOR TO MATCH EXISTING WIRE SIZES
E-37 | P21-1210B | 2" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT1 | JBOX2 | EXISTING | SERVES 21-FCV-1210; CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 21-FCV-1310; CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 21-FCV-1410; CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 22-FCV-2301; CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 22-FCV-2302; CONTRACTOR TO MATCH EXISTING WIRE SIZES
E-37 | P21-1210C | 2" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | JBOX2 | P-VLT4 | EXISTING | SERVES 21-FCV-1210; CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 21-FCV-1310; CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 21-FCV-1410; CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 22-FCV-2301; CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 22-FCV-2302; CONTRACTOR TO MATCH EXISTING WIRE SIZES
E-37 | P21-1210D | 2" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT4 | J-BOX4 | EXISTING | SERVES 21-FCV-1210; CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 21-FCV-1310; CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 21-FCV-1410; CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 22-FCV-2301; CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 22-FCV-2302; CONTRACTOR TO MATCH EXISTING WIRE SIZES
E-37 | P21-1210E | 1" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | J-BOX4 | DS-21-FCV-1210 (BV5 DISC) |  | CONTRACTOR TO PULL NEW WIRE TO DISCONNECT MATCHING EXISTING SIZES; RE-USE EXISTING CONDUIT (EXISTING CONDUIT PC-13) | SERVES 21-FCV-1210
|  |  | 3 #10 W/ #10 GND | [7 empty] | SERVES 21-FCV-1310
|  |  | 3 #10 W/ #10 GND | [7 empty] | SERVES 21-FCV-1410
E-37 | P21-1300A | 2" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | MCC-3 | P-VLT1 | DB-10 | SERVES 21-ME-1300 (POWER, HOA, JSH, JSHH, DISCONNECT AUX); CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 5 #14 | CONTROL
|  |  | 3 #10 W/ #10 GND | 480VAC | [5 empty] | SERVES 22-P-1300; CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 3 #8 W/ #10 GND | [6 empty] | SERVES 22-P-2300; CONTRACTOR TO MATCH EXISTING WIRE SIZES
E-37 | P21-1300B | 2" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | P-VLT1 | J-BOX2 | EXISTING | SERVES 21-ME-1300 (POWER, HOA, JSH, JSHH, DISCONNECT AUX); CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 5 #14 | CONTROL
|  |  | 3 #10 W/ #10 GND | 480VAC | [5 empty] | SERVES 22-P-1300; CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 3 #8 W/ #10 GND | [6 empty] | SERVES 22-P-2300; CONTRACTOR TO MATCH EXISTING WIRE SIZES
E-37 | P21-1300C | 2" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | J-BOX2 | P-VLT4 | EXISTING | SERVES 21-ME-1300 (POWER, HOA, JSH, JSHH, DISCONNECT AUX); CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 5 #14 | CONTROL
|  |  | 3 #10 W/ #10 GND | 480VAC | [5 empty] | SERVES 22-P-1300; CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 3 #8 W/ #10 GND | [6 empty] | SERVES 22-P-2300; CONTRACTOR TO MATCH EXISTING WIRE SIZES
E-37 | P21-1300D | 2" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | P-VLT4 | J-BOX4 | EXISTING | SERVES 21-ME-1300 (POWER, HOA, JSH, JSHH, DISCONNECT AUX); CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 5 #14 | CONTROL
|  |  | 3 #10 W/ #10 GND | 480VAC | [5 empty] | SERVES 22-P-1300; CONTRACTOR TO MATCH EXISTING WIRE SIZES
|  |  | 3 #8 W/ #10 GND | [6 empty] | SERVES 22-P-2300; CONTRACTOR TO MATCH EXISTING WIRE SIZES
E-37 | P21-1300E | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | J-BOX4 | DS-21-ME-1300 |  | CONTRACTOR TO PULL NEW WIRE TO DISCONNECT MATCHING EXISTING SIZES; RE-USE EXISTING CONDUIT (EXISTING CONDUIT PC-12)
|  |  | 5 #14 | CONTROL
E-37 | P21-1305 | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | J-BOX4 | 21-LIT-1305B |  | POWERED BY SAME CIRCUITS FOUND IN P21-1204C
E-37 | P21-1310 | 1" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | DS-21-FCV-1210 (BV5 DISC) | DS-21-FCV-1310 (BV6 DISC) |  | CONTRACTOR TO PULL NEW WIRE TO DISCONNECT MATCHING EXISTING SIZES; RE-USE EXISTING CONDUIT (EXISTING CONDUIT PC-13) | SERVES 21-FCV-1310
|  |  | 3 #10 W/ #10 GND | [7 empty] | SERVES 21-FCV-1410
E-37 | P21-1410 | 1" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | DS-21-FCV-1310 (BV6 DISC) | DS-21-FCV-1410 (BV7 DISC) |  | CONTRACTOR TO PULL NEW WIRE TO DISCONNECT MATCHING EXISTING SIZES ; RE-USE EXISTING CONDUIT (EXISTING CONDUIT PC-13)
E-37 | P22-1200 | 1" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | J-BOX3 | DS-22-P-1200 (SP1 DISC) |  | CONTRACTOR TO PULL NEW WIRE TO DISCONNECT MATCHING EXISTING SIZES; RE-USE EXISTING CONDUIT (EXISTING CONDUIT PC-6)
E-37 | P22-1204A | 2" | 2 #10 W/ #10 GND | 120VAC | PVC GRS | PVC 40 | LP-MCC3 | P-VLT1 | DB-10 | SERVES POSSIBLE L1, L2, L3, L4, L5, L6, L8, L9; CONTRACTOR TO DETERMINE WHICH LIGHTS ARE POWERED HERE
E-37 | P22-1204B | 2" | 2 #10 W/ #10 GND | 120VAC | PVC GRS | PVC 40 | P-VLT1 | J-BOX2 | EXISTING | SERVES POSSIBLE L1, L2, L3, L4, L5, L6, L8, L9; CONTRACTOR TO DETERMINE WHICH LIGHTS ARE POWERED HERE
E-37 | P22-1204C | 2" | 2 #10 W/ #10 GND | 120VAC | PVC GRS | PVC 40 | J-BOX2 | P-VLT4 | EXISTING | SERVES POSSIBLE L1, L2, L3, L4, L5, L6, L8, L9; CONTRACTOR TO DETERMINE WHICH LIGHTS ARE POWERED HERE
E-37 | P22-1204D | 2" | 2 #10 W/ #10 GND | 120VAC | PVC GRS | PVC 40 | P-VLT3 | J-BOX3 | EXISTING | CONTRACTOR TO PULL NEW WIRE TO J-BOX4 MATCHING EXISTING SIZES, INSTALL TERMINAL BLOCKS AND INTERCEPT EXISTING WIRE; SERVES POSSIBLE L1, L2, L3, L4, L5, L6, L8, L9 (EXISTING CONDUIT PC-30); CONTRACTOR TO DETERMINE WHICH LIGHTS ARE POWERED HERE
E-37 | P22-1300 | 1" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | J-BOX4 | DS-22-P-1300 (SP2 DISC) |  | CONTRACTOR TO PULL NEW WIRE TO DISCONNECT MATCHING EXISTING SIZES; RE-USE EXISTING CONDUIT (EXISTING CONDUIT PC-11)
E-37 | P22-2200 | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | J-BOX3 | DS-22-P-2200 (SCP1 DISC) |  | CONTRACTOR TO PULL NEW WIRE TO DISCONNECT MATCHING EXISTING SIZES; RE-USE EXISTING CONDUIT (EXISTING CONDUIT PC-5)
E-37 | P22-2201A | 2" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | DP-MCC3 | P-VLT1 | DB-10 | SERVES 22-FCV-2201
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 22-FCV-2202
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 51-G-1101
E-37 | P22-2201B | 2" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT1 | J-BOX2 | EXISTING | SERVES 22-FCV-2201
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 22-FCV-2202
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 51-G-1101
E-37 | P22-2201C | 2" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | J-BOX2 | P-VLT4 | EXISTING | SERVES 22-FCV-2201
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 22-FCV-2202
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 51-G-1101
E-37 | P22-2201D | 2" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT4 | J-BOX3 | EXISTING | SERVES 22-FCV-2201
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 22-FCV-2202
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 51-G-1101
E-37 | P22-2201E | 2" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | J-BOX3 | P-VLT3 | EXISTING | SERVES 51-G-1101
E-37 | P22-2201F | 2" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT3 | P-VLT2 | EXISTING | SERVES 51-G-1101
E-37 | P22-2201G | 1" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | J-BOX3 | DC-22-FCV-2201 (PV1 DISC) |  | CONTRACTOR TO PULL NEW WIRE TO DISCONNECT MATCHING EXISTING SIZES; RE-USE EXISTING CONDUIT (EXISTING CONDUIT PC-3)
E-37 | P22-2202 | 1" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | J-BOX3 | DC-22-FCV-2202 (PV2 DISC) |  | CONTRACTOR TO PULL NEW WIRE TO DISCONNECT MATCHING EXISTING SIZES; RE-USE EXISTING CONDUIT (EXISTING CONDUIT PC-4)
E-37 | P22-2300 | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | J-BOX4 | DS-22-P-2300 (SCP2 DISC) |  | CONTRACTOR TO PULL NEW WIRE TO DISCONNECT MATCHING EXISTING SIZES; RE-USE EXISTING CONDUIT (EXISTING CONDUIT PC-10)
E-37 | P22-2301 | 1" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | J-BOX4 | DS-22-FCV-2301 (PV3 DISC) |  | CONTRACTOR TO PULL NEW WIRE TO DISCONNECT MATCHING EXISTING SIZES; RE-USE EXISTING CONDUIT (EXISTING CONDUIT PC-8)
E-37 | P22-2302 | 1" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | J-BOX4 | DS-22-FCV-2302 (PV4 DISC) |  | CONTRACTOR TO PULL NEW WIRE TO DISCONNECT MATCING EXISTING SIZES; RE-USE EXISTING CONDUIT (EXISTING CONDUIT PC-9)
E-39 | P23-1000A | 1.25" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | LP-AB | P-VLT25 | DB-4 | SERVES 23-FIT-1010
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 23-FIT-1020
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 23-LIT-1002
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 61-LIT-1000
E-39 | P23-1000B | 1.25" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SERVES 23-FIT-1010
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 23-FIT-1020
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 23-LIT-1002
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 61-LIT-1000
E-39 | P23-1000C | 1.25" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | P-VLT26 | JB-23-1000 | DB-15 | SERVES 23-FIT-1010
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 23-FIT-1020
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 23-LIT-1002
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 61-LIT-1000
E-39 | P23-1002 | 3/4" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | JB-23-1000 | 23-LIT-1002
E-39 | P23-1010 | 3/4" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | JB-23-1000 | 23-FIT-1010
E-39 | P23-1020 | 3/4" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | JB-23-1000 | 23-FIT-1020 |  |  |  | 2222222222
POWER CONDUIT | [11 empty] | 33333333333 | 1
SHEET | CONDUIT | SIZE | CONDUCTORS | SERVICE | AG MATERIAL | UG MATERIAL | FROM | TO | DUCTBANKS | NOTES |  |  | 2
E-40 | P23-1100A | 1" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | MCC-AB1 | P-VLT25 | DB-4 |  |  |  | 3
E-40 | P23-1100B | 1" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 |  |  |  | 3
E-40 | P23-1100C | 1" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT26 | DS-23-P-1100 | DB-15 |  |  |  | 3
E-40 | P23-1100D | 3/4" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | DS-23-P-1100 | 23-P-1100 |  |  |  |  | 4
E-40 | P23-1200A | 1" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | MCC-AB4 | P-VLT25 | DB-4 |  |  |  | 5
E-40 | P23-1200B | 1" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 |  |  |  | 5
E-40 | P23-1200C | 1" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT26 | DS-23-P-1200 | DB-15 |  |  |  | 5
E-40 | P23-1200D | 3/4" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | DS-23-P-1200 | 23-P-1200 |  |  |  |  | 6
E-40 | P23-1300A | 1.5" | 3 #3 W/ #8 GND | 480VAC | PVC GRS | PVC 40 | MCC-AB1 | P-VLT25 | DB-4 |  |  |  | 7
E-40 | P23-1300B | 1.5" | 3 #3 W/ #8 GND | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 |  |  |  | 7
E-40 | P23-1300C | 1.5" | 3 #3 W/ #8 GND | 480VAC | PVC GRS | PVC 40 | P-VLT26 | DS-23-P-1300 | DB-15 |  |  |  | 7
E-40 | P23-1300D | 1.5" | 3 #3 W/ #8 GND | 480VAC | PVC GRS | PVC 40 | DS-23-P-1300 | 23-P-1300 |  |  |  |  | 8
E-40 | P23-1400A | 1.5" | 3 #3 W/ #8 GND | 480VAC | PVC GRS | PVC 40 | MCC-AB1 | P-VLT25 | DB-4 |  |  |  | 7
E-40 | P23-1400B | 1.5" | 3 #3 W/ #8 GND | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 |  |  |  | 7
E-40 | P23-1400C | 1.5" | 3 #3 W/ #8 GND | 480VAC | PVC GRS | PVC 40 | P-VLT26 | DS-23-P-1400 | DB-15 |  |  |  | 7
E-40 | P23-1400D | 1.5" | 3 #3 W/ #8 GND | 480VAC | PVC GRS | PVC 40 | DS-23-P-1400 | 23-P-1400 |  |  |  |  | 8
E-40 | P23-1500A | 1.5" | 3 #3 W/ #8 GND | 480VAC | PVC GRS | PVC 40 | MCC-AB4 | P-VLT25 | DB-4 |  |  |  | 7
E-40 | P23-1500B | 1.5" | 3 #3 W/ #8 GND | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 |  |  |  | 7
E-40 | P23-1500C | 1.5" | 3 #3 W/ #8 GND | 480VAC | PVC GRS | PVC 40 | P-VLT26 | DS-23-P-1500 | DB-15 |  |  |  | 7
E-40 | P23-1500D | 1.5" | 3 #3 W/ #8 GND | 480VAC | PVC GRS | PVC 40 | DS-23-P-1500 | 23-P-1500 |  |  |  |  | 8
E-36 | P23-2100A | 1" | 3#12 W/#12 GND | 480VAC | PVC GRS | PVC 40 | MCC-AB2 | P-VLT28 | DB-6
E-42 | P23-2100B | 1" | 3#12 W/#12 GND | 480VAC | PVC GRS | PVC 40 | P-VLT28 | JB-23-2000 | DB-9
E-42 | P23-2100C | 1" | 3#12 W/#12 GND | 480VAC | PVC GRS | PVC 41 | JB-23-2000 | DS-23-2100
E-36 | P23-2200A | 1" | 3#12 W/#12 GND | 480VAC | PVC GRS | PVC 40 | MCC-AB2 | P-VLT28 | DB-6
E-42 | P23-2200B | 1" | 3#12 W/#12 GND | 480VAC | PVC GRS | PVC 40 | P-VLT28 | JB-23-2000 | DB-9
E-42 | P23-2200C | 1" | 3#12 W/#12 GND | 480VAC | PVC GRS | PVC 41 | JB-23-2000 | DS-23-2200
E-38 | P23-2300A | 1" | 3#12 W/#12 GND | 480VAC | PVC GRS | PVC 40 | MCC-AB3 | P-VLT28 | DB-6
E-42 | P23-2300B | 1" | 3#12 W/#12 GND | 480VAC | PVC GRS | PVC 40 | P-VLT28 | JB-23-2000 | DB-9
E-42 | P23-2300C | 1" | 3#12 W/#12 GND | 480VAC | PVC GRS | PVC 41 | JB-23-2000 | DS-23-2300
E-39 | P31-1001A | 2" | 1 - #12 3C TC | 120VAC | PVC GRS | PVC 40 | LP-AB | P-VLT25 | DB-4 | SERVES 31-AIT-1001/31-AIT-1002 |  |  | 64
|  |  | 1 - #12 3C TC | [6 empty] | SERVES 31-AIT-1010 |  |  | 65
E-39 | P31-1001B | 2" | 1 - #12 3C TC | 120VAC | PVC GRS | PVC 40 | P-VLT25 | JB-31-1000 |  | SERVES 31-AIT-1001/31-AIT-1002 |  |  | 64
|  |  | 1 - #12 3C TC | [6 empty] | SERVES 31-AIT-1010 |  |  | 65
E-39 | P31-1001C | 3/4" | 1 - #12 3C TC | 120VAC | PVC GRS | PVC 40 | JB-31-1000 | 31-AIT-1001/31-AIT-1002 |  | VIA CABLE TRAY 31-1000 |  |  | 71
E-39 | P31-1010 | 3/4" | 1 - #12 3C TC | 120VAC | PVC GRS | PVC 40 | JB-31-1000 | 31-AIT-1010 |  | VIA CABLE TRAY 31-1001 |  |  | 72
E-36 | P31-1100A | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | MCC-AB2 | P-VLT25 | DB-4 |  |  |  | 73
E-36 | P31-1100B | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | P-VLT25 | JB-31-1000 |  |  |  |  | 73
E-36 | P31-1100C | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | JB-31-1000 | DS-31-ME-1100 |  | VIA CABLE TRAY 31-1000 |  |  | 74
E-36 | P31-1100D | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | DS-31-ME-1100 | 31-ME-1100 |  |  |  |  | 75
E-36 | P31-1200A | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | MCC-AB2 | P-VLT25 | DB-4 |  |  |  | 73
E-36 | P31-1200B | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | P-VLT25 | JB-31-1000 |  |  |  |  | 73
E-36 | P31-1200C | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | JB-31-1000 | DS-31-ME-1200 |  | VIA CABLE TRAY 31-1000 |  |  | 76
E-36 | P31-1200D | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | DS-31-ME-1200 | 31-ME-1200
E-36 | P31-1300A | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | MCC-AB2 | P-VLT25 | DB-4
E-36 | P31-1300B | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | P-VLT25 | JB-31-1000
E-36 | P31-1300C | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | JB-31-1000 | DS-31-ME-1300 |  | VIA CABLE TRAY 31-1000
E-36 | P31-1300D | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | DS-31-ME-1300 | 31-ME-1300
E-36 | P31-1400A | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | MCC-AB2 | P-VLT25 | DB-4
E-36 | P31-1400B | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | P-VLT25 | JB-31-1000
E-36 | P31-1400C | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | JB-31-1000 | DS-31-ME-1400 |  | VIA CABLE TRAY 31-1000
E-36 | P31-1400D | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | DS-31-ME-1400 | 31-ME-1400
E-39 | P31-2001A | 2" | 1 - #12 3C TC | 120VAC | PVC GRS | PVC 40 | LP-AB | P-VLT25 | DB-4 | SERVES 31-AIT-2001/31-AIT-2002
|  |  | 1 - #12 3C TC | [6 empty] | SERVES 31-AIT-2010/31-AIT-3010
|  |  | 1 - #12 3C TC | [6 empty] | SERVES 31-AIT-3001/31-AIT-3002
E-39 | P31-2001B | 2" | 1 - #12 3C TC | 120VAC | PVC GRS | PVC 40 | P-VLT25 | JB-31-2000 |  | SERVES 31-AIT-2001/31-AIT-2002
|  |  | 1 - #12 3C TC | [6 empty] | SERVES 31-AIT-2010/31-AIT-3010
|  |  | 1 - #12 3C TC | [6 empty] | SERVES 31-AIT-3001/31-AIT-3002
E-39 | P31-2001C | 3/4" | 1 - #12 3C TC | 120VAC | PVC GRS | PVC 40 | JB-31-2000 | 31-AIT-2001, 31-AIT-2002 |  | VIA CABLE TRAY 31-2000
E-39 | P31-2010 | 3/4" | 1 - #12 3C TC | 120VAC | PVC GRS | PVC 40 | JB-31-2000 | 31-AIT-2010, 31-AIT-3010 |  | VIA CABLE TRAY 31-2001
E-36 | P31-2100A | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | MCC-AB2 | P-VLT25 | DB-4
E-36 | P31-2100B | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | P-VLT25 | JB-31-2000 | DB-14
E-36 | P31-2100C | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | JB-31-2000 | DS-31-ME-2100 |  | VIA CABLE TRAY 31-2000
E-36 | P31-2100D | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | DS-31-ME-2100 | 31-ME-2100
E-36 | P31-2200A | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | MCC-AB2 | P-VLT25 | DB-4
E-36 | P31-2200B | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | P-VLT25 | JB-31-2000 | DB-14
E-36 | P31-2200C | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | JB-31-2000 | DS-31-ME-2200 |  | VIA CABLE TRAY 31-2000
E-36 | P31-2200D | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | DS-31-ME-2200 | 31-ME-2200
E-36 | P31-2300A | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | MCC-AB2 | P-VLT25 | DB-4
E-36 | P31-2300B | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | P-VLT25 | JB-31-2000 | DB-14
E-36 | P31-2300C | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | JB-31-2000 | DS-31-ME-2300 |  | VIA CABLE TRAY 31-2000
E-36 | P31-2300D | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | DS-31-ME-2300 | 31-ME-2300
E-36 | P31-2400A | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | MCC-AB2 | P-VLT25 | DB-4
E-36 | P31-2400B | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | P-VLT25 | JB-31-2000 | DB-14
E-36 | P31-2400C | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | JB-31-2000 | DS-31-ME-2400 |  | VIA CABLE TRAY 31-2000
E-36 | P31-2400D | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | DS-31-ME-2400 | 31-ME-2400
E-39 | P31-3001 | 3/4" | 1 - #12 3C TC | 120VAC | PVC GRS | PVC 40 | JB-31-2000 | 31-AIT-3001, 31-AIT-3002 |  | VIA CABLE TRAY 31-2000 |  |  | 3
E-38 | P31-3100A | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | MCC-AB3 | P-VLT25 | DB-4 |  |  |  | 4
E-38 | P31-3100B | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | P-VLT25 | JB-31-2000 | DB-14 |  |  |  | 5
E-38 | P31-3100C | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | JB-31-2000 | DS-31-ME-3100 |  | VIA CABLE TRAY 31-2000 |  |  | 6
E-38 | P31-3100D | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | DS-31-ME-3100 | 31-ME-3100 |  |  |  |  | 7
E-38 | P31-3200A | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | MCC-AB3 | P-VLT25 | DB-4 |  |  |  | 4
E-38 | P31-3200B | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | P-VLT25 | JB-31-2000 | DB-14 |  |  |  | 5
E-38 | P31-3200C | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | JB-31-2000 | DS-31-ME-3200 |  | VIA CABLE TRAY 31-2000 |  |  | 8
E-38 | P31-3200D | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | DS-31-ME-3200 | 31-ME-3200 |  |  |  |  | 9
E-38 | P31-3300A | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | MCC-AB3 | P-VLT25 | DB-4 |  |  |  | 10
E-38 | P31-3300B | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | P-VLT25 | JB-31-2000 | DB-14 |  |  |  | 11
E-38 | P31-3300C | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | JB-31-2000 | DS-31-ME-3300 |  | VIA CABLE TRAY 31-2000 |  |  | 12
E-38 | P31-3300D | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | DS-31-ME-3300 | 31-ME-3300 |  |  |  |  | 13
E-38 | P31-3400A | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | MCC-AB3 | P-VLT25 | DB-4 |  |  |  | 4
E-38 | P31-3400B | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | P-VLT25 | JB-31-2000 | DB-14 |  |  |  | 5
E-38 | P31-3400C | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | JB-31-2000 | DS-31-ME-3400 |  | VIA CABLE TRAY 31-2000 |  |  | 14
E-38 | P31-3400D | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | DS-31-ME-3400 | 31-ME-3400 |  |  |  | 33333333333333 | 15
POWER CONDUIT | [11 empty] | 444444444444 | 1
SHEET | CONDUIT | SIZE | CONDUCTORS | SERVICE | AG MATERIAL | UG MATERIAL | FROM | TO | DUCTBANKS | NOTES |  |  | 2
E-39 | P31-4001A | 2" | 2 - #12 3C TC | 120VAC | PVC GRS | PVC 40 | LP-AB | P-VLT25 |  | SERVES 31-AIT-4001/31-AIT-4002, 31-AIT-4010 |  |  | 16
E-39 | P31-4001B | 2" | 2 - #12 3C TC | 120VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 |  | SERVES 31-AIT-4001/31-AIT-4002, 31-AIT-4010 |  |  | 16
E-39 | P31-4001C | 2" | 2 - #12 3C TC | 120VAC | PVC GRS | PVC 40 | P-VLT26 | JB-31-4000 |  | SERVES 31-AIT-4001/31-AIT-4002, 31-AIT-4010 |  |  | 16
E-39 | P31-4001D | 3/4" | 1 - #12 3C TC | 120VAC | PVC GRS | PVC 40 | JB-31-4000 | 31-AIT-4001, 31-AIT-4002 |  | VIA CABLE TRAY 31-4000 |  |  | 17
E-39 | P31-4010 | 3/4" | 1 - #12 3C TC | 120VAC | PVC GRS | PVC 40 | JB-31-4000 | 31-AIT-4010 |  | VIA CABLE TRAY 31-4001 |  |  | 18
E-38 | P31-4100A | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | MCC-AB3 | P-VLT25 | DB-4 |  |  |  | 19
E-38 | P31-4100B | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 |  |  |  | 20
E-38 | P31-4100C | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | P-VLT26 | JB-31-4000 |  |  |  |  | 21
E-38 | P31-4100D | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | JB-31-4000 | DS-31-ME-4200 |  | VIA CABLE TRAY 31-4000 |  |  | 22
E-38 | P31-4100E | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | DS-31-ME-4200 | 31-ME-4200 |  |  |  |  | 23
E-38 | P31-4200A | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | MCC-AB3 | P-VLT25 | DB-4 |  |  |  | 19
E-38 | P31-4200B | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 |  |  |  | 20
E-38 | P31-4200C | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | P-VLT26 | JB-31-4000 |  |  |  |  | 21
E-38 | P31-4200D | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | JB-31-4000 | DS-31-ME-4200 |  | VIA CABLE TRAY 31-4000 |  |  | 24
E-38 | P31-4200E | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | DS-31-ME-4200 | 31-ME-4200 |  |  |  |  | 25
E-38 | P31-4300A | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | MCC-AB3 | P-VLT25 | DB-4 |  |  |  | 19
E-38 | P31-4300B | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 |  |  |  | 20
E-38 | P31-4300C | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | P-VLT26 | JB-31-4000 |  |  |  |  | 21
E-38 | P31-4300D | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | JB-31-4000 | DS-31-ME-4300 |  | VIA CABLE TRAY 31-4000 |  |  | 29
E-38 | P31-4300E | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | DS-31-ME-4300 | 31-ME-4300 |  |  |  |  | 30
E-38 | P31-4400A | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | MCC-AB3 | P-VLT25 | DB-4 |  |  |  | 19
E-38 | P31-4400B | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 |  |  |  | 20
E-38 | P31-4400C | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | P-VLT26 | JB-31-4000 |  |  |  |  | 21
E-38 | P31-4400D | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | JB-31-4000 | DS-31-ME-4400 |  | VIA CABLE TRAY 31-4000 |  |  | 31
E-38 | P31-4400E | 1" | VFD RATED TRAY CABLE (3 #10 W/ #10 GND) | 480VAC | PVC GRS | PVC 40 | DS-31-ME-4400 | 31-ME-4400 |  |  |  |  | 32
E-38 | P31-4550A | 2" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | DP-AB2 | P-VLT25 | DB-4 | SERVES 31-G-4550 |  |  | 33
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 31-G-4560 |  |  | 34
E-38 | P31-4550B | 2" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SERVES 31-G-4550 |  |  | 35
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 31-G-4560 |  |  | 36
E-38 | P31-4550C | 2" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT26 | JB-31-4000 |  | SERVES 31-G-4550 |  |  | 37
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 31-G-4560 |  |  | 38
E-37 | P31-4550D | 3/4" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | JB-31-4000 | DS-31-G-4550 |  |  |  |  | 39
E-37 | P31-4550E | 3/4" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | DS-31-G-4550 | 31-G-4550 |  |  |  |  | 40
E-38 | P31-4560A | 3/4" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | JB-31-4000 | DS-31-G-4560 |  |  |  |  | 41
E-38 | P31-4560B | 3/4" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | DS-31-G-4560 | 31-G-4560 |  |  |  |  | 42
E-36 | P31-5300A | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | MCC-AB2 | P-VLT25 | DB-4 |  |  |  | 43
E-36 | P31-5300B | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 |  |  |  | 43
E-36 | P31-5300C | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT26 | DS-31-BLR-5300 | DB-15 |  |  |  | 43
E-36 | P31-5300D | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | DS-31-BLR-5300 | 31-BLR-5300 |  |  |  |  | 44
E-38 | P31-5400A | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | MCC-AB3 | P-VLT25 | DB-4 |  |  |  | 43
E-38 | P31-5400B | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 |  |  |  | 43
E-38 | P31-5400C | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | MCC-AB3 | DS-31-BLR-5400 | DB-15 |  |  |  | 45
E-38 | P31-5400D | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | DS-31-BLR-5400 | 31-BLR-5400 |  |  |  |  | 46
E-39 | P31-5500A | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | LP-AB | P-VLT25 | DB-4 | SERVES FUTURE METHANOL PUMP |  |  | 47
E-39 | P31-5500B | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | P-VLT25 | JB-31-2000 | DB-14 | SERVES FUTURE METHANOL PUMP |  |  | 48
E-39 | P31-5500C | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | JB-31-2000 | JB-31-5500 |  | SERVES FUTURE METHANOL PUMP (VIA CABLE TRAY 31-2000)
E-39 | P31-5500D | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | JB-31-5500 | 120V RECEPTACLES |  | SERVES FUTURE METHANOL PUMP
E-41 | P32-1100A | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | MCC-AB3 | P-VLT25 | DB-4
E-41 | P32-1100B | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14
E-41 | P32-1100C | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | P-VLT26 | JB-32-1100 | DB-16
E-41 | P32-1100D | 3/4" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | JB-32-1100 | DS-32-ME-1100
E-41 | P32-1100E | 3/4" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | DS-32-ME-1100 | 32-ME-1100
E-41 | P32-1200A | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | MCC-AB2 | P-VLT25 | DB-4
E-41 | P32-1200B | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14
E-41 | P32-1200C | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | P-VLT26 | JB-32-1100 | DB-16
E-41 | P32-1200D | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | JB-32-1100 | JB-32-1200 | DB-17
E-41 | P32-1200E | 3/4" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | JB-32-1200 | DS-32-ME-1200
E-41 | P32-1200F | 3/4" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | DS-32-ME-1200 | 32-ME-1200
E-41 | P32-1101A | 1" | 4 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | LP-AB | P-VLT25 | DB-4 | SERVES SC1 LIGHT AND OUTLET; LIGHTS ARE TO BE ROUTED THROUGH THE LIGHTING CONTROL PANEL (LCP-AB)
|  |  | 4 #12 W/ #12 GND | [6 empty] | SERVES SC2 LIGHT AND OUTLET; LIGHTS ARE TO BE ROUTED THROUGH THE LIGHTING CONTROL PANEL (LCP-AB)
|  |  | 4 #12 W/ #12 GND | [6 empty] | FUTURE SERVES SC3 LIGHT AND OUTLET; LIGHTS ARE TO BE ROUTED THROUGH THE LIGHTING CONTROL PANEL (LCP-AB)
E-41 | P32-1101B | 1" | 4 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SERVES SC1 LIGHT AND OUTLET; LIGHTS ARE TO BE ROUTED THROUGH THE LIGHTING CONTROL PANEL (LCP-AB)
|  |  | 4 #12 W/ #12 GND | [6 empty] | SERVES SC2 LIGHT AND OUTLET; LIGHTS ARE TO BE ROUTED THROUGH THE LIGHTING CONTROL PANEL (LCP-AB)
|  |  | 4 #12 W/ #12 GND | [6 empty] | FUTURE SERVES SC3 LIGHT AND OUTLET; LIGHTS ARE TO BE ROUTED THROUGH THE LIGHTING CONTROL PANEL (LCP-AB)
E-41 | P32-1101C | 1" | 4 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | P-VLT26 | JB-32-1100 | DB-16 | SERVES SC1 LIGHT AND OUTLET
|  |  | 4 #12 W/ #12 GND | [6 empty] | SERVES SC2 LIGHT AND OUTLET
E-41 | P32-1201 | 1" | 4 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | JB-32-1100 | JB-32-1200 | DB-17 | SERVES SC2 LIGHT AND OUTLET
E-41 | P32-1300A | 1" | FUTURE | 480VAC | PVC GRS | PVC 40 | MCC-AB3 | P-VLT25 | DB-4
E-41 | P32-1300B | 1" | FUTURE | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14
E-41 | P32-1300C | 1" | FUTURE | 480VAC | PVC GRS | PVC 40 | P-VLT26 | P-VLT27 | DB-15
E-39 | P33-1100A | 2" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | DP-AB2 | P-VLT25 | DB-4 | SERVES 33-G-1100 |  |  | 26
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 33-G-1200 |  |  | 27
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 33-G-1300 |  |  | 28
E-39 | P33-1100B | 2" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SERVES 33-G-1100 |  |  | 26
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 33-G-1200 |  |  | 27
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 33-G-1300 |  |  | 28
E-39 | P33-1100C | 2" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT26 | JB-23-1000 | DB-15 | SERVES 33-G-1100 |  |  | 26
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 33-G-1200 |  |  | 27
|  |  | 3 #10 W/ #10 GND | [6 empty] | SERVES 33-G-1300 |  |  | 28
E-39 | P33-1100D | 3/4" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | JB-23-1000 | DS-33-G-1100 |  |  |  |  | 30
E-39 | P33-1100E | 3/4" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | DS-33-G-1100 | 33-G-1100 |  |  |  |  | 31
E-39 | P33-1200A | 3/4" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | JB-23-1000 | DS-33-G-1200 |  |  |  |  | 32
E-39 | P33-1200B | 3/4" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | DS-33-G-1200 | 33-G-1200 |  |  |  |  | 33
E-41 | P36-1000A | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | LP-AB | P-VLT25 | DB-4 |  |  |  | 4
E-41 | P36-1000B | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 |  |  |  | 4
E-41 | P36-1000C | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | P-VLT26 | P-VLT27 | DB-15 |  |  |  | 4
E-41 | P36-1000D | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | P-VLT27 | 36-FIT-1000 | DB-36 |  |  |  | 4
E-41 | P36-1100A | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | MCC-AB2 | P-VLT25 | DB-4 | SERVES 36-P-1100 |  |  | 10
E-41 | P36-1100B | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SERVES 36-P-1100 |  |  | 11
E-41 | P36-1100C | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT26 | P-VLT27 | DB-15 | SERVES 36-P-1100 |  |  | 12
E-41 | P36-1100D | 1" | 3 #4 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT27 | DS-36-P-1100 | DB-36 | SERVES 36-P-1100 |  |  | 13
E-41 | P36-1100E | 1" | 3 #4 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | DS-36-P-1100 | 36-P-1100 |  |  |  |  | 14
E-41 | P36-1200A | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | MCC-AB2 | P-VLT25 | DB-4 | SERVES 36-P-1200 |  |  | 10
E-41 | P36-1200B | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SERVES 36-P-1200 |  |  | 11
E-41 | P36-1200C | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT26 | P-VLT27 | DB-15 | SERVES 36-P-1200 |  |  | 12
E-41 | P36-1200D | 1" | 3 #4 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT27 | DS-36-P-1200 | DB-36 | SERVES 36-P-1200 |  |  | 13
E-41 | P36-1200E | 1" | 3 #4 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | DS-36-P-1200 | 36-P-1200 |  |  |  |  | 14
POWER CONDUIT | [11 empty] | 44444444444 | 1
SHEET | CONDUIT | SIZE | CONDUCTORS | SERVICE | AG MATERIAL | UG MATERIAL | FROM | TO | DUCTBANKS | NOTES |  | 55555555555 | 2
E-41 | P36-1300A | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | MCC-AB3 | P-VLT25 | DB-4 | SERVES 36-P-1300 |  |  | 10
E-41 | P36-1300B | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SERVES 36-P-1300 |  |  | 11
E-41 | P36-1300C | 1" | 3 #8 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT26 | P-VLT27 | DB-15 | SERVES 36-P-1300 |  |  | 12
E-41 | P36-1300D | 1" | 3 #4 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT27 | DS-36-P-1300 | DB-36 | SERVES 36-P-1300 |  |  | 13
E-41 | P36-1300E | 1" | 3 #4 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | DS-36-P-1300 | 36-P-1300 |  |  |  |  | 14
E-41 | P36-1400A | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | DP-AB2 | P-VLT25 | DB-4 | SERVES 36-V-1400
|  |  | 3 #12 W/ #12 GND | [6 empty] | SERVES 36-V-1410
E-41 | P36-1400B | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SERVES 36-V-1400
|  |  | 3 #12 W/ #12 GND | [6 empty] | SERVES 36-V-1410
E-41 | P36-1400C | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | P-VLT26 | P-VLT27 | DB-15 | SERVES 36-V-1400
|  |  | 3 #12 W/ #12 GND | [6 empty] | SERVES 36-V-1410
E-41 | P36-1400D | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | P-VLT27 | DS-36-V-1400 | DB-36
E-41 | P36-1400E | 3/4" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | DS-36-V-1400 | 36-V-1400
E-41 | P36-1410A | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | P-VLT27 | DS-36-V-1410 | DB-36
E-41 | P36-1410B | 3/4" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | DS-36-V-1410 | 36-V-1410
E-41 | P41-1000 | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | LP-AB | V#20P | DB-33 | CONTRACTOR TO INTERCEPT EXISTING ROUTE ( V#20P --> V#21P) TO LIGHT AND PULL NEW WIRE
|  |  | 2 #12 W/ #12 GND | [6 empty] | CONTRACTOR TO INTERCEPT EXISTING ROUTE (V#19P --> V#20P --> V#21P) TO RECEPTACLE AND PULL NEW WIRE
E-42 | P41-1100 | 1" | 3 #12 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | DB-AB2 | V#20P | DB-33 | CONTRACTOR TO VERIFY EXISTING ROUTE (V#20P --> DS-41-SG-1100; USES CONDUIT P930) AND PULL NEW WIRE; SERVES 41-SG-1100
|  |  | 3 #12 W/ #10 GND | [6 empty] | CONTRACTOR TO VERIFY EXISTING ROUTE (V#20P --> V#21P; USES P930 TO V#20P THEN P922 TO V#21P THEN P925 TO VALVE LOCATION) SERVES 51-SG-1200
|  |  | 3 #12 W/ #10 GND | [6 empty] | CONTRACTOR TO VERIFY EXISTING ROUTE (V#20P --> V#21P --> DS-41-SG-2110; USES CONDUIT SP25 AND P923) AND PULL NEW WIRE; SERVES 41-SG-2110
|  |  | 3 #12 W/ #10 GND | [6 empty] | CONTRACTOR TO VERIFY EXISTING ROUTE (V#20P --> V#21P; USES P922 TO V#21P THEN P925 TO DISCONNECT; SERVES 41-G-2120
E-42 | P41-2110 | 1" | 3 #12 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | DS-41-G-2110 | 41-G-2110
E-42 | P41-2120 | 1" | 3 #12 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | DS-41-G-2120 | 41-G-2120
E-42 | P42-1120 | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | PLC-PRP | 42-FIT-1120 |  | VIA TRENCH
E-43 | P43-1000A | 1.5" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | LP-AB | P-VLT28 | DB-6 | SERVES 43-LIT-1101
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 43-LIT-1102
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 43-AIT-1300
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 43-AIT-1310
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 43-AIT-1320
E-43 | P43-1000B | 1.5" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | P-VLT28 | JB-43-1000 | DB-7 | SERVES 43-LIT-1101
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 43-LIT-1102
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 43-AIT-1300
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 43-AIT-1310
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 43-AIT-1320
E-43 | P43-1100A | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | LP-AB | P-VLT28 | DB-6 | SERVES 43-P-1100
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 43-P-1200
E-43 | P43-1100B | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | P-VLT28 | JB-43-1000 | DB-7 | SERVES 43-P-1100
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 43-P-1200
E-38 | P43-1200A | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | LP-AB | P-VLT28 | DB-6 | SERVES SODIUM BISULFITE TANK 1 HEAT TRACE
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES SODIUM BISULFITE TANK 2 HEAT TRACE
E-38 | P43-1200B | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | P-VLT28 | JB-43-1000 | DB-7 | SERVES SODIUM BISULFITE TANK 1 HEAT TRACE
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES SODIUM BISULFITE TANK 2 HEAT TRACE
E-38 | P43-1200C | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | JB-43-1000 | SODIUM BISULFITE TANK HEAT TRACE |  | SERVES SODIUM BISULFITE TANK 1 HEAT TRACE
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES SODIUM BISULFITE TANK 2 HEAT TRACE
E-43 | P43-1400A | 2" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | LP-AB | P-VLT28 | DB-6 | SERVES INDOOR LIGHTING
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES INDOOR RECEPTACLES
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES OUTDOOR LIGHTING
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES OUTDOOR RECEPTACLES
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 43-ME-1510
E-43 | P43-1400B | 2" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | P-VLT28 | JB-43-1000 | DB-7 | SERVES INDOOR LIGHTING
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES INDOOR RECEPTACLES
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES OUTDOOR LIGHTING
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES OUTDOOR RECEPTACLES
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 43-ME-1510
E-43 | P43-1100C | 3/4" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | JB-43-1000 | 43-P-1100
| P43-1200 | 3/4" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | JB-43-1000 | 43-P-1200
E-43 | P43-1101 | 3/4" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | JB-43-1000 | 43-LIT-1101
E-43 | P43-1102 | 3/4" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | JB-43-1000 | 43-LIT-1102
E-43 | P43-1300 | 3/4" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | JB-43-1000 | 43-AIT-1300
E-43 | P43-1310 | 3/4" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | JB-43-1000 | 43-AIT-1310
E-43 | P43-1320 | 3/4" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | JB-43-1000 | 43-AIT-1320
E-43 | P43-H1510 | 3/4" | 3 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | JB-43-1000 | 43-ME-1510
E-43 | P43-H1520A | 1" | 3 #12 W/ #12 GND | 240VAC | PVC GRS | PVC 40 | LP-AB | P-VLT28 | DB-6
E-43 | P43-H1520B | 1" | 3 #12 W/ #12 GND | 240VAC | PVC GRS | PVC 40 | P-VLT28 | JB-43-1000 | DB-7
E-43 | P43-H1520C | 1" | 3 #12 W/ #12 GND | 240VAC | PVC GRS | PVC 40 | JB-43-1000 | 43-ME-1520
E-43 | P43-H1510 | 1" | 3 #12 W/ #12 GND | 240VAC | PVC GRS | PVC 40 | JB-43-1000 | 43-ME-1520
E-42 | P44-1000A | 1" | 3 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | LP-AB | 44-FIT-1000
E-42 | P44-1000B | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | LP-AB | V#20P | DB-33
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 44-M-1000 VAULT SUMP PUMP
E-42 | P44-1000C | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | V#20P | SPARE | DB-21
|  |  | 2 #12 W/ #12 GND |  |  |  |  | DEDICATED OUTLET INSIDE VAULT |  | SERVES 44-M-1000 VAULT SUMP PUMP
E-41 | P44-1100A | 1" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | MCC-AB2 | DS-44-H-1100 | DB-5
E-41 | P44-1100B | 3/4" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | DS-44-H-1100 | 44-H-1100
E-41 | P44-1310A | 1" | #12 4C TC | 480VAC | GRS | PVC 40 | DP-AB2 | DS-44-G-1310 | DB-5 | VIA CABLE TRAY 44-1000;
E-41 | P44-1310B | 3/4" | #12 4C TC | 480VAC | GRS | PVC 40 | DS-44-G-1310 | 44-G-1310
E-41 | P44-1320A | 1" | #12 4C TC | 480VAC | GRS | PVC 40 | DP-AB2 | DS-44-G-1320 | DB-5 | VIA CABLE TRAY 44-1000;
E-41 | P44-1320B | 3/4" | #12 4C TC | 480VAC | GRS | PVC 40 | DS-44-G-1320 | 44-G-1320
E-41 | P44-1330A | 1" | #12 4C TC | 480VAC | GRS | PVC 40 | DP-AB2 | DS-44-G-1330 | DB-5 | VIA CABLE TRAY 44-1000;
E-41 | P44-1330B | 3/4" | #12 4C TC | 480VAC | GRS | PVC 40 | DS-44-G-1330 | 44-G-1330
E-41 | P44-1340A | 1" | #12 4C TC | 480VAC | GRS | PVC 40 | DP-AB2 | DS-44-G-1340 | DB-5 | VIA CABLE TRAY 44-1000;
E-41 | P44-1340B | 3/4" | #12 4C TC | 480VAC | GRS | PVC 40 | DS-44-G-1340 | 44-G-1340
E-41 | P44-1350A | 1" | #12 4C TC | 480VAC | GRS | PVC 40 | DP-AB2 | DS-44-G-1350 | DB-5 | VIA CABLE TRAY 44-1000;
E-41 | P44-1350B | 3/4" | #12 4C TC | 480VAC | GRS | PVC 40 | DS-44-G-1340 | 44-G-1350
E-36 | P44-1510A | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | MCC-AB2 | DS-44-H-1510 | DB-5
E-36 | P44-1510B | 3/4" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | DS-44-H-1510 | 44-H-1510
E-38 | P44-1520A | 3/4" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | MCC-AB3 | DS-44-H-1520 | DB-5
E-38 | P44-1520B | 3/4" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | DS-44-H-1520 | 44-H-1520 |  |  |  | 55555555
POWER CONDUIT | [11 empty] | 66666666666 | 1
SHEET | CONDUIT | SIZE | CONDUCTORS | SERVICE | AG MATERIAL | UG MATERIAL | FROM | TO | DUCTBANKS | NOTES |  |  | 2
E-41 | P44-1611 | 3/4" | #12 3C TC | 120VAC | GRS | PVC 40 | PLC-AB | 44-H-1611 | DB-5 | VIA CABLE TRAY 44-1000;
E-41 | P44-1621 | 3/4" | #12 3C TC | 120VAC | GRS | PVC 40 | PLC-AB | 44-H-1621 | DB-5 | VIA CABLE TRAY 44-1000;
E-41 | P44-1631 | 3/4" | #12 3C TC | 120VAC | GRS | PVC 40 | PLC-AB | 44-H-1631 | DB-5 | VIA CABLE TRAY 44-1000;
E-41 | P44-1900 | 3/4" | #12 3C TC | 120VAC | GRS | PVC 40 | LP-UV-2 | 44-P-1900 |  | VIA CABLE TRAY 44-1000;
E-41 | P44-1920 | 3/4" | #12 3C TC | 120VAC | GRS | PVC 40 | LP-UV-2 | 44-FIT-1920 |  | VIA CABLE TRAY 44-1000;
E-37 | P51-1000 | 1" | 2 #10 W/ #10 GND | 120/240VAC | PVC GRS | PVC 40 | P-VLT2 | L9 | EXISTING | CONTRACTOR TO TERMINATE NEW WIRE TO EXISTING LIGHT
E-42 | P51-1006 | 1" | 3 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | LP-RWDP | 51-FIT-1006
E-42 | P51-1007 | 1" | 3 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | LP-RWDP | 51-FIT-1007
E-42 | P51-1009A | 1" | 3 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | LP-AB | 51-FIT-1009
E-42 | P51-1009B | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | LP-AB | V#20P | DB-33
|  |  | 2 #12 W/ #12 GND | [6 empty] | SERVES 51-M-1009 VAULT SUMP PUMP
E-42 | P51-1009C | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | V#20P | SPARE | DB-21
|  |  | 2 #12 W/ #12 GND |  |  |  |  | DEDICATED OUTLET INSIDE VAULT |  | SERVES 51-M-1009 VAULT SUMP PUMP
E-37 | P51-1101A | 1" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | P-VLT2 | DS-51-FCV-1101 (PCE-WG2 DISC) | EXISTING | CONTRACTOR TO INSTALL NEW CONDUIT AND PULL NEW WIRE TO DISCONNECT
E-37 | P51-1101B | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | P-VLT2 | 51-LIT-1101 | EXISTING
E-41 | P51A | 4-4" | 3 SETS OF (3 - 400 MCM W/ 3/0 NEUT AND 350 MCM GND) | 480VAC | PVC GRS | PVC 40 | SWBD-AB1 | P-VLT25 | DB-4
E-41 | P51B | 4-4" | 3 SETS OF (3 - 400 MCM W/ 3/0 NEUT AND 350 MCM GND) | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14
E-41 | P51C | 4-4" | 3 SETS OF (3 - 400 MCM W/ 3/0 NEUT AND 350 MCM GND) | 480VAC | PVC GRS | PVC 40 | P-VLT26 | P-VLT27 | DB-15
E-41 | P51D | 4-4" | 3 SETS OF (3 - 400 MCM W/ 3/0 NEUT AND 350 MCM GND) | 480VAC | PVC GRS | PVC 40 | P-VLT27 | DP-RWDP | DB-18
E-41 | P51-2100A | 3" | 3 4/0 W/ #2 GND | 480VAC | PVC GRS | PVC 40 | DP-RWDP | VFD-51-P-2100
E-41 | P51-2100B | 3" | 3 4/0 W/ #2 GND | 480VAC | PVC GRS | PVC 40 | VFD-51-P-2100 | 51-P-2100
E-41 | P51-2200A | 3" | 3 4/0 W/ #2 GND | 480VAC | PVC GRS | PVC 40 | DP-RWDP | VFD-51-P-2200
E-41 | P51-2200B | 3" | 3 4/0 W/ #2 GND | 480VAC | PVC GRS | PVC 40 | VFD-51-P-2200 | 51-P-2200
E-41 | P51-2300A | 3" | 3 4/0 W/ #2 GND | 480VAC | PVC GRS | PVC 40 | DP-RWDP | VFD-51-P-2300
E-41 | P51-2300B | 3" | 3 4/0 W/ #2 GND | 480VAC | PVC GRS | PVC 40 | VFD-51-P-2300 | 51-P-2200
E-41 | P51-2400A | 3" | 3 4/0 W/ #2 GND | 480VAC | PVC GRS | PVC 40 | DP-RWDP | VFD-51-P-2400
E-41 | P51-2400B | 3" | 3 4/0 W/ #2 GND | 480VAC | PVC GRS | PVC 40 | VFD-51-P-2400 | 51-P-2200
E-41 | P51-2510C | 3/4" | 3 #12 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | DP-RWDP | DS-51-V-2510
E-41 | P51-2510D | 3/4" | 3 #12 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | DS-51-V-2510 | 51-V-2510
E-40 | P52-0003 | 1.5" | 3 #4 W/ #8 GND; 2 #14 | 480VAC | PVC GRS | PVC 40 | MCC-RW2 | BL-M-1, TSH-52-0003 |  | RE-USE EXISTING CONDUIT, PULL IN NEW WIRE
E-40 | P52-0004 | 1.5" | 3 #4 W/ #8 GND; 2 #14 | 480VAC | PVC GRS | PVC 40 | MCC-RW2 | BL-M-2, TSH-52-0004 |  | RE-USE EXISTING CONDUIT, PULL IN NEW WIRE
E-40 | P52-1013A | 3" | 3 250 MCM W/ #4 GND | 480VAC | PVC GRS | PVC 40 | MCC-AB1 | VFD-52-P-1013
E-40 | P52-1013B | 2" | 3 3/0 W/ #6 GND | 480VAC | PVC GRS | PVC 40 | VFD-52-P-1013 | P-VLT28 | DB-6
E-40 | P52-1013C | 2" | 3 3/0 W/ #6 GND | 480VAC | PVC GRS | PVC 40 | P-VLT28 | 52-P-1013 | DB-9
E-40 | P52-1014A | 3" | 3 250 MCM W/ #4 GND | 480VAC | PVC GRS | PVC 40 | MCC-AB4 | VFD-52-P-1014 |  |  |  |  | 3
E-40 | P52-1014B | 2" | 3 3/0 W/ #6 GND | 480VAC | PVC GRS | PVC 40 | VFD-52-P-1014 | P-VLT28 | DB-6 |  |  |  | 4
E-40 | P52-1014C | 2" | 3 3/0 W/ #6 GND | 480VAC | PVC GRS | PVC 40 | P-VLT28 | 52-P-1014 | DB-9 |  |  |  | 5
E-40 | P52-1221 | 2" | 3 #1 W/ #6 GND; 2 #14 | 480VAC | PVC GRS | PVC 40 | MCC-RW2 | 52-P-1221 |  | RE-USE EXISTING CONDUIT, PULL IN NEW WIRE |  |  | 6
E-40 | P52-1222 | 2" | 3 #1 W/ #6 GND; 2 #14 | 480VAC | PVC GRS | PVC 40 | MCC-RW2 | 52-P-1222 |  | RE-USE EXISTING CONDUIT, PULL IN NEW WIRE |  |  | 7
E-40 | P52-1223 | 2" | 3 #1 W/ #6 GND; 2 #14 | 480VAC | PVC GRS | PVC 40 | MCC-RW2 | 52-P-1223 |  | RE-USE EXISTING CONDUIT, PULL IN NEW WIRE |  |  | 8
E-40 | P52-1229 | 3/4" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | MCC-RW1 | 52-V-1229 |  |  |  |  | 9
E-40 | P52-1228 | 3/4" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | MCC-RW1 | 52-V-1228 |  |  |  |  | 10
E-40 | P52-1200 | 3/4" | 3 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | LP-RWTF | 52-AIT-1200
E-40 | P52-1250 | 3/4" | 3 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | LP-RWTF | 52-AIT-1250
E-36 | P61-1000 | 1" | 3 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | JB-23-1000 | 61-LIT-1000
E-36 | P61-1100A | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | MCC-AB2 | P-VLT25 | DB-4
E-36 | P61-1100B | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14
E-36 | P61-1100C | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | P-VLT26 | DS-61-P-1100 | DB-15
E-36 | P61-1100D | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | DS-61-P-1100 | 61-P-1100
E-38 | P61-1200A | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | MCC-AB3 | P-VLT25 | DB-4
E-38 | P61-1200B | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14
E-38 | P61-1200C | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | P-VLT26 | DS-61-P-1200 | DB-15
E-38 | P61-1200D | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | DS-61-P-1200 | 61-P-1200
E-36 | P61-1300A | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | MCC-AB2 | P-VLT25 | DB-4
E-36 | P61-1300B | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14
E-36 | P61-1300C | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | P-VLT26 | DS-61-P-1300 | DB-15
E-36 | P61-1300D | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | DS-61-P-1300 | 61-P-1300 |  | WAS DRAIN BOX SUMP
E-42 | P62-2100 | 1" | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | MCC-3 | LCP-62-ME-2100 | DB-25
E-42 | P62-2600 | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | LCP-62-ME-2100 | 62-P-2600
E-42 | P62-1100 | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | LCP-62-ME-2100 | 62-ME-1100
E-42 | P62-2100 | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | LCP-62-ME-2100 | 62-ME-2100
E-42 | P62-2200 | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | LCP-62-ME-2100 | 62-ME-2200
E-42 | P62-2300 | 1" | 3 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | LCP-62-ME-2100 | 62-P-2300
E-42 | P62-2500 | 1" | 2 #12 W/ #12 GND | 120VAC | PVC GRS | PVC 40 | LCP-62-ME-2100 | 62-FIT-2500
E-42 | P62-2620 | 1" | 2 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | LP-AB | 62-FIT-2620 | DB-25
E-42 | P62-2640 | 1" | 2 #12 W/ #12 GND | 480VAC | PVC GRS | PVC 40 | LP-AB | 62-FIT-2640 | DB-25
E-41 | P922 | 2" | 3 #10 W/ #10 GND | 480VAC | N/A | N/A | V#20P | V#21P | N/A | EXISTING CONDUIT USED TO 51-G-1210
|  |  | 3 #10 W/ #10 GND | [6 empty] | EXISTING CONDUIT USED TO 51-SG-1200
|  |  | 3 #10 W/ #10 GND | [6 empty] | EXISTING CONDUIT USED TO 51-G-2120
E-42 | P923 | EX | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | V#21P | DS-41-G-2110 |  | SERVES 41-G-2110
E-42 | P925 | EX | 3 #10 W/ #10 GND | 480VAC | PVC GRS | PVC 40 | V#21P | DS-41-G-2120 |  | SERVES 41-G-2120 - UTILIZE OTHER HALF OF P925 - P925 ENTERS AND EXITS V#21P
E-41 | P925 | EX | 3 #10 W/ #10 GND | 480VAC | N/A | N/A | V#21P | DS-51-G-1210 | N/A | EXISTING CONDUIT USED TO 51-G-1210
|  |  | 3 #10 W/ #10 GND |  |  |  |  | DS-51-SG-1200 |  | EXISTING CONDUIT USED TO 51-SG-1200
E-42 | P930 | 2" | 3 #10 W/ #10 GND | 480VAC | N/A | N/A | V#19P | V#20P | N/A | EXISTING CONDUIT USED TO 41-SG-1100
|  |  | 3 #10 W/ #10 GND | [6 empty] | EXISTING CONDUIT USED TO 51-SG-1200
|  |  | 3 #10 W/ #10 GND | [6 empty] | EXISTING CONDUIT USED TO 51-G-1210
|  | 2" | 3 #10 W/ #10 GND | 480VAC | N/A | N/A | V#20P | DS-41-SG-1100 | N/A | EXISTING CONDUIT USED TO 41-SG-1100
E-42 | P9A1 | 2" | 4 #14 | CONTROL | N/A | N/A | V#12P | 51-G-1210 |  | EXISTING CONDUIT USED TO 51-G-1210 (OPEN/CLOSE COMMAND)
|  |  | 4 #14 |  |  |  |  | 51-SG-1200 |  | EXISTING CONDUIT USED TO 51-SG-1200 (OPEN/CLOSE COMMAND) |  | 666666666666
CONTROL CONDUIT | [11 empty] | 77777777777
SHEET | CONDUIT | SIZE | CONDUCTORS | SERVICE | AG MATERIAL | UG MATERIAL | FROM | TO | DUCTBANKS | NOTES
E-36 | C002A | 1" | 10 #14 | CONTROL | PVC GRS | PVC 40 | PLC-AB | ATS |  | 5 #14 FROM THE MAIN GENERATOR, 5 #14 FROM THE MAIN ATS
E-36 | C002B | 1" | 7 #14 | CONTROL | PVC GRS | PVC 40 | ATS | MAIN GENERATOR | DB-3 | 2 #14 TO GO TO THE ATS, 5 #14 TO GO TO EXISTING HEADWORKS PLC
E-38 | C015 | 3/4" | MFG CABLE | CONTROL | GRS | PVC 40 | 31-H-1110 | 31-H-1100
E-38 | C019 | 3/4" | MFG CABLE | CONTROL | GRS | PVC 40 | 31-H-1210 | 31-H-1200
E-42 | C300 | 1" | 8 #14 | CONTROL | PVC GRS | PVC 40 | EX CONTROL PANEL | PLC-PSP |  | SERVES 41-G-2110 (OPEN/CLOSE COMMANDS)
E-42 | C400 | 1" | 10 #14 | CONTROL | PVC GRS | PVC 40 | EX MCC | PLC-PRP |  | SERVES 41-G-2110 (OPEN/CLOSE COMMANDS)
E-42 | C906 | EX | 4 #14 | CONTROL | PVC GRS | PVC 40 | 41-G-2110 | V#21S |  | SERVES 41-G-2110 (OPEN/CLOSE COMMANDS)
E-40 | C23-1100A | 1" | 14 # 14 | CONTROL | PVC GRS | PVC 40 | MCC-AB1 | P-VLT25 | DB-4 | SERVES 23-P-1100 (HOR, MMS, TSH, ENABLE, SV, FSL)
E-40 | C23-1100B | 1" | 14 # 14 | CONTROL | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SERVES 23-P-1100 (HOR, MMS, TSH, ENABLE, SV, FSL)
E-40 | C23-1100C | 1" | 14 # 14 | CONTROL | PVC GRS | PVC 40 | P-VLT26 | LCP-23-P-1100 | DB-15 | SERVES 23-P-1100 (HOR, MMS, TSH, ENABLE, SV, FSL)
E-40 | C23-1100D | 3/4" | 4 #14 | CONTROL | PVC GRS | PVC 40 | LCP-23-P-1100 | 23-MMS/TSH-1100
E-40 | C23-1100E | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-23-P-1100 | DS-23-P-1100
E-40 | C23-1100F | 3/4" | 4 #14 | CONTROL | PVC GRS | PVC 40 | LCP-23-P-1100 | 23-SV-1100, 23-FSL-1100
E-40 | C23-1100G | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-23-P-1100 | 23-ZSC-1100
E-40 | C23-1200A | 1" | 14 # 14 | CONTROL | PVC GRS | PVC 40 | MCC-AB4 | P-VLT25 | DB-4 | SERVES 23-P-1200 (HOR, MMS, TSH, ENABLE, SV, FSL)
E-40 | C23-1200B | 1" | 14 # 14 | CONTROL | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SERVES 23-P-1200 (HOR, MMS, TSH, ENABLE, SV, FSL)
E-40 | C23-1200C | 1" | 14 # 14 | CONTROL | PVC GRS | PVC 40 | P-VLT26 | LCP-23-P-1200 | DB-15 | SERVES 23-P-1200 (HOR, MMS, TSH, ENABLE, SV, FSL)
E-40 | C23-1200D | 3/4" | 4 #14 | CONTROL | PVC GRS | PVC 40 | LCP-23-P-1200 | 23-MMS/TSH-1200
E-40 | C23-1200E | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-23-P-1200 | DS-23-P-1200
E-40 | C23-1200F | 3/4" | 4 #14 | CONTROL | PVC GRS | PVC 40 | LCP-23-P-1200 | 23-SV-1200, 23-FSL-1200
E-40 | C23-1200G | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-23-P-1200 | 23-ZSC-1200
E-40 | C23-1300A | 1" | 14 # 14 | CONTROL | PVC GRS | PVC 40 | MCC-AB1 | P-VLT25 | DB-4 | SERVES 23-P-1300 (HOR, MMS, TSH, ENABLE, SV, FSL)
E-40 | C23-1300B | 1" | 14 # 14 | CONTROL | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SERVES 23-P-1300 (HOR, MMS, TSH, ENABLE, SV, FSL)
E-40 | C23-1300C | 1" | 14 # 14 | CONTROL | PVC GRS | PVC 40 | P-VLT26 | LCP-23-P-1300 | DB-15 | SERVES 23-P-1300 (HOR, MMS, TSH, ENABLE, SV, FSL)
E-40 | C23-1300D | 3/4" | 4 #14 | CONTROL | PVC GRS | PVC 40 | LCP-23-P-1300 | 23-MMS/TSH-1300
E-40 | C23-1300E | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-23-P-1300 | DS-23-P-1300
E-40 | C23-1300F | 3/4" | 4 #14 | CONTROL | PVC GRS | PVC 40 | LCP-23-P-1300 | 23-SV-1300, 23-FSL-1300
E-40 | C23-1300G | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-23-P-1300 | 23-ZSC-1300
E-40 | C23-1400A | 1" | 14 # 14 | CONTROL | PVC GRS | PVC 40 | MCC-AB1 | P-VLT25 | DB-4 | SERVES 23-P-1400 (HOR, MMS, TSH, ENABLE, SV, FSL)
E-40 | C23-1400B | 1" | 14 # 14 | CONTROL | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SERVES 23-P-1400 (HOR, MMS, TSH, ENABLE, SV, FSL)
E-40 | C23-1400C | 1" | 14 # 14 | CONTROL | PVC GRS | PVC 40 | P-VLT26 | LCP-23-P-1400 | DB-15 | SERVES 23-P-1400 (HOR, MMS, TSH, ENABLE, SV, FSL)
E-40 | C23-1400D | 3/4" | 4 #14 | CONTROL | PVC GRS | PVC 40 | LCP-23-P-1400 | 23-MMS/TSH-1400
E-40 | C23-1400E | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-23-P-1400 | DS-23-P-1400
E-40 | C23-1400F | 3/4" | 4 #14 | CONTROL | PVC GRS | PVC 40 | LCP-23-P-1400 | 23-SV-1400, 23-FSL-1400
E-40 | C23-1400G | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-23-P-1400 | 23-ZSC-1400
E-40 | C23-1500A | 1" | 14 # 14 | CONTROL | PVC GRS | PVC 40 | MCC-AB4 | P-VLT25 | DB-4 | SERVES 23-P-1500 (HOR, MMS, TSH, ENABLE, SV, FSL)
E-40 | C23-1500B | 1" | 14 # 14 | CONTROL | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SERVES 23-P-1500 (HOR, MMS, TSH, ENABLE, SV, FSL)
E-40 | C23-1500C | 1" | 14 # 14 | CONTROL | PVC GRS | PVC 40 | P-VLT26 | LCP-23-P-1500 | DB-15 | SERVES 23-P-1500 (HOR, MMS, TSH, ENABLE, SV, FSL)
E-40 | C23-1500D | 3/4" | 4 #14 | CONTROL | PVC GRS | PVC 40 | LCP-23-P-1500 | 23-MMS/TSH-1500
E-40 | C23-1500E | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-23-P-1500 | DS-23-P-1500
E-40 | C23-1500F | 3/4" | 4 #14 | CONTROL | PVC GRS | PVC 40 | LCP-23-P-1500 | 23-SV-1500, 23-FSL-1500
E-40 | C23-1500F | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-23-P-1500 | 23-ZSC-1500
E-36 | C31-1100A | 2" | 4 - #14 8C TC | CONTROL | PVC GRS | PVC 40 | MCC-AB2 | P-VLT25 | DB-4 | SERVES LCP-31-ME-1100, LCP-31-ME-1200, LCP-31-ME-1300, LCP-31-ME-1400
E-36 | C31-1100B | 2" | 4 - #14 8C TC | CONTROL | PVC GRS | PVC 40 | P-VLT25 | JB-31-1000 |  | SERVES LCP-31-ME-1100, LCP-31-ME-1200, LCP-31-ME-1300, LCP-31-ME-1400
E-36 | C31-1100C | 1" | 1 - #14 8C TC | CONTROL | PVC GRS | PVC 40 | JB-31-1000 | LCP-31-ME-1100 |  | VIA CABLE TRAY 31-1000
E-36 | C31-1100D | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-31-ME-1100 | 31-TSH-1100
E-36 | C31-1100E | 2" | 24 #14 | 50VDC | PVC GRS | PVC 40 | MCC-AB2 | A-VLT25 | DB-4 | SERVES AERATION BASIN 1 AND 2 WHEEL BRAKES
|  |  | 24 $14 |  |  |  | MCC-AB3 |  |  | SERVES AERATION BASIN 3 AND 4 WHEEL BRAKES
E-36 | C31-1100F | 1" | 12 #14 | 50VDC | PVC GRS | PVC 40 | A-VLT25 | JB-31-1001 |  | ONLY 3 #14 GO TO 31-ME-1100 BRAKE WHILE THE OTHER 9 #14 GO TO THE OTHER 3 WHEELS
E-36 | C31-1100G | 1" | 12 #14 | 50VDC | PVC GRS | PVC 40 | JB-31-1001 | 31-ME-1100 BRAKE |  | ONLY 3 #14 GO TO 31-ME-1100 BRAKE WHILE THE OTHER 9 #14 GO TO THE OTHER 3 WHEELS
E-36 | C31-1200A | 1" | 1 - #14 8C TC | CONTROL | PVC GRS | PVC 40 | JB-31-1000 | LCP-31-ME-1200 |  | VIA CABLE TRAY 31-1000
E-36 | C31-1200B | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-31-ME-1200 | 31-TSH-1200
E-36 | C31-1200C | 3/4" | 3 #14 | 50VDC | PVC GRS | PVC 40 | C31-1100E | 31-ME-1200 BRAKE
E-36 | C31-1300A | 1" | 1 - #14 8C TC | CONTROL | PVC GRS | PVC 40 | JB-31-1000 | LCP-31-ME-1300 |  | VIA CABLE TRAY 31-1000
E-36 | C31-1300B | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-31-ME-1300 | 31-TSH-1300
E-36 | C31-1300C | 3/4" | 3 #14 | 50VDC | PVC GRS | PVC 40 | C31-1100E | 31-ME-1300 BRAKE
E-36 | C31-1400A | 1" | 1 - #14 8C TC | CONTROL | PVC GRS | PVC 40 | JB-31-1000 | LCP-31-ME-1400 |  | VIA CABLE TRAY 31-1000
E-36 | C31-1400B | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-31-ME-1400 | 31-TSH-1400
E-36 | C31-1400C | 3/4" | 3 #14 | 50VDC | PVC GRS | PVC 40 | C31-1100E | 31-ME-1400 BRAKE
E-36 | C31-2100A | 2" | 4 - #14 8C TC | CONTROL | PVC GRS | PVC 40 | MCC-AB2 | P-VLT25 | DB-4 | SERVES LCP-31-ME-2100, LCP-31-ME-2200, LCP-31-ME-2300, LCP-31-ME-2400
E-36 | C31-2100B | 2" | 4 - #14 8C TC | CONTROL | PVC GRS | PVC 40 | P-VLT25 | JB-31-2000 | DB-14 | SERVES LCP-31-ME-2100, LCP-31-ME-2200, LCP-31-ME-2300, LCP-31-ME-2400
E-36 | C31-2100C | 1" | 1 - #14 8C TC | CONTROL | PVC GRS | PVC 40 | JB-31-2000 | LCP-31-ME-2100 |  | VIA CABLE TRAY 31-2000
E-36 | C31-2100D | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-31-ME-2100 | 31-TSH-2100
E-36 | C31-2100E | 2" | 8 - #14 4C TC | 50VDC | PVC GRS | PVC 40 | A-VLT25 | JB-31-2001 |  | SERVES AERATION BASIN 2 AND 3 WHEELS
E-36 | C31-2100F | 3/4" | 1 - #14 3C TC | 50VDC | PVC GRS | PVC 40 | JB-31-2001 | 31-ME-2100 BRAKE |  | VIA CABLE TRAY 31-2000
E-36 | C31-2200A | 1" | 1 - #14 8C TC | CONTROL | PVC GRS | PVC 40 | JB-31-2000 | LCP-31-ME-2200 |  | VIA CABLE TRAY 31-2000
E-36 | C31-2200B | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-31-ME-2200 | 31-TSH-2200
E-36 | C31-2200C | 3/4" | 1 - #14 3C TC | 50VDC | PVC GRS | PVC 40 | JB-31-2001 | 31-ME-2200 BRAKE |  | VIA CABLE TRAY 31-2000
E-36 | C31-2300A | 1" | 1 - #14 8C TC | CONTROL | PVC GRS | PVC 40 | JB-31-2000 | LCP-31-ME-2300 |  | VIA CABLE TRAY 31-2000
E-36 | C31-2300B | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-31-ME-2300 | 31-TSH-2300
E-36 | C31-2300C | 3/4" | 1 - #14 3C TC | 50VDC | PVC GRS | PVC 40 | JB-31-2001 | 31-ME-2300 BRAKE |  | VIA CABLE TRAY 31-2000
E-36 | C31-2400A | 1" | 1 - #14 8C TC | CONTROL | PVC GRS | PVC 40 | JB-31-2000 | LCP-31-ME-2400 |  | VIA CABLE TRAY 31-2000
E-36 | C31-2400B | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-31-ME-2400 | 31-TSH-2400
E-36 | C31-2400C | 3/4" | 1 - #14 3C TC | 50VDC | PVC GRS | PVC 40 | JB-31-2001 | 31-ME-2400 BRAKE |  | VIA CABLE TRAY 31-2000
E-38 | C31-3100A | 2" | 4 - #14 8C TC | CONTROL | PVC GRS | PVC 40 | MCC-AB3 | P-VLT25 | DB-4 | SERVES LCP-31-ME-3100, LCP-31-ME-3200, LCP-31-ME-3300, LCP-31-ME-3400
E-38 | C31-3100B | 2" | 4 - #14 8C TC | CONTROL | PVC GRS | PVC 40 | P-VLT25 | JB-31-2000 | DB-14 | SERVES LCP-31-ME-3100, LCP-31-ME-3200, LCP-31-ME-3300, LCP-31-ME-3400
E-38 | C31-3100C | 1" | 1 - #14 8C TC | CONTROL | PVC GRS | PVC 40 | JB-31-2000 | LCP-31-ME-3100 |  | VIA CABLE TRAY 31-2000
E-38 | C31-3100D | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-31-ME-3100 | 31-TSH-3100
E-38 | C31-3100E | 3/4" | 1 - #14 3C TC | 50VDC | PVC GRS | PVC 40 | JB-31-2001 | 31-ME-3100 BRAKE |  | VIA CABLE TRAY 31-2000
E-38 | C31-3200A | 1" | 1 - #14 8C TC | CONTROL | PVC GRS | PVC 40 | JB-31-2000 | LCP-31-ME-3200 |  | VIA CABLE TRAY 31-2000
E-38 | C31-3200B | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-31-ME-3200 | 31-TSH-3200
E-38 | C31-3200C | 3/4" | 1 - #14 3C TC | 50VDC | PVC GRS | PVC 40 | JB-31-2001 | 31-ME-3200 BRAKE |  | VIA CABLE TRAY 31-2000
E-38 | C31-3300A | 1" | 1 - #14 8C TC | CONTROL | PVC GRS | PVC 40 | JB-31-2000 | LCP-31-ME-3300 |  | VIA CABLE TRAY 31-2000
E-38 | C31-3300B | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-31-ME-3300 | 31-TSH-3300
E-38 | C31-3300C | 3/4" | 1 - #14 3C TC | 50VDC | PVC GRS | PVC 40 | JB-31-2001 | 31-ME-3300 BRAKE |  | VIA CABLE TRAY 31-2000
E-38 | C31-3400A | 1" | 1 - #14 8C TC | CONTROL | PVC GRS | PVC 40 | JB-31-2000 | LCP-31-ME-3400 |  | VIA CABLE TRAY 31-2000
E-38 | C31-3400B | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-31-ME-3400 | 31-TSH-3400
E-38 | C31-3400C | 3/4" | 1 - #14 3C TC | 50VDC | PVC GRS | PVC 40 | JB-31-2001 | 31-ME-3400 BRAKE |  | VIA CABLE TRAY 31-2000
CONTROL CONDUIT | [11 empty] | 77777777777777 | 1
SHEET | CONDUIT | SIZE | CONDUCTORS | SERVICE | AG MATERIAL | UG MATERIAL | FROM | TO | DUCTBANKS | NOTES |  | 8888888888888 | 2
E-38 | C31-4100A | 2" | 4 - #14 8C TC | CONTROL | PVC GRS | PVC 40 | MCC-AB3 | P-VLT25 | DB-4 | SERVES LCP-31-ME-4200, LCP-31-ME-4200, LCP-31-ME-4300, LCP-31-ME-4400 |  |  | 3
E-38 | C31-4100B | 2" | 4 - #14 8C TC | CONTROL | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SERVES LCP-31-ME-4200, LCP-31-ME-4200, LCP-31-ME-4300, LCP-31-ME-4400 |  |  | 4
E-38 | C31-4100C | 2" | 4 - #14 8C TC | CONTROL | PVC GRS | PVC 40 | P-VLT26 | JB-31-4000 |  | SERVES LCP-31-ME-4200, LCP-31-ME-4200, LCP-31-ME-4300, LCP-31-ME-4400 |  |  | 5
E-38 | C31-4100D | 1" | 1 - #14 8C TC | CONTROL | PVC GRS | PVC 40 | JB-31-4000 | LCP-31-ME-4200 |  | VIA CABLE TRAY 31-4000 |  |  | 6
E-38 | C31-4100E | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-31-ME-4200 | 31-TSH-4100 |  |  |  |  | 7
E-38 | C31-4100F | 1" | 12 #14 | 50VDC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SERVES AERATION BASIN 4 WHEEL BRAKES |  |  | 8
E-38 | C31-4100G | 1" | 12 #14 | 50VDC | PVC GRS | PVC 40 | P-VLT26 | JB-31-4001 |  | SERVES AERATION BASIN 4 WHEEL BRAKES |  |  | 8
E-38 | C31-4100H | 1" | 3 #14 | 50VDC | PVC GRS | PVC 40 | JB-31-4001 | 31-ME-4200 BRAKE |  | ONLY 3 #14 GO TO 31-ME-4200 BRAKE WHILE THE OTHER 9 #14 GO TO THE OTHER 3 WHEELS |  |  | 9
E-38 | C31-4200A | 1" | 1 - #14 8C TC | CONTROL | PVC GRS | PVC 40 | JB-31-4000 | LCP-31-ME-4200 |  | VIA CABLE TRAY 31-4000 |  |  | 10
E-38 | C31-4200B | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-31-ME-4200 | 31-TSH-4200 |  |  |  |  | 11
E-38 | C31-4200C | 3/4" | 3 #14 | 50VDC | PVC GRS | PVC 40 | C31-4100G | 31-ME-4200 BRAKE |  |  |  |  | 12
E-38 | C31-4300A | 1" | 1 - #14 8C TC | CONTROL | PVC GRS | PVC 40 | JB-31-4000 | LCP-31-ME-4300 |  | VIA CABLE TRAY 31-4000 |  |  | 13
E-38 | C31-4300B | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-31-ME-4300 | 31-TSH-4300 |  |  |  |  | 14
E-38 | C31-4300C | 3/4" | 3 #14 | 50VDC | PVC GRS | PVC 40 | C31-4100G | 31-ME-4300 BRAKE |  |  |  |  | 15
E-38 | C31-4400A | 1" | 1 - #14 8C TC | CONTROL | PVC GRS | PVC 40 | JB-31-4000 | LCP-31-ME-4400 |  | VIA CABLE TRAY 31-4000 |  |  | 16
E-38 | C31-4400B | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-31-ME-4400 | 31-TSH-4400 |  |  |  |  | 17
E-38 | C31-4400C | 3/4" | 3 #14 | 50VDC | PVC GRS | PVC 40 | C31-4100G | 31-ME-4400 BRAKE |  |  |  |  | 18
E-36 | C31-5300A | 1" | 2 #14 | CONTROL | PVC GRS | PVC 40 | MCC-AB2 | P-VLT25 | DB-4 | SERVES 31-BLR-5300 (ENABLE)
E-36 | C31-5300B | 1" | 2 #14 | CONTROL | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SERVES 31-BLR-5300 (ENABLE)
E-36 | C31-5300C | 1" | 2 #14 | CONTROL | PVC GRS | PVC 40 | P-VLT25 | DS-31-BLR-5300 | DB-15 | SERVES 31-BLR-5300 (ENABLE)
E-36 | C31-5400 | 1" | 2 #14 | CONTROL | PVC GRS | PVC 40 | DS-31-BLR-5300 | 31-BLR-5400 |  | SERVES 31-BLR-5400 (ENABLE)
E-41 | C32-1100A | 1.5" | 5 #14 | CONTROL | PVC GRS | PVC 40 | MCC-AB2/MCC-AB3 | P-VLT25 | DB-4 | SERVES 32-ME-1100 (HOR, JSH, JSHH)
|  |  | 5 #14 | [6 empty] | SERVES 32-ME-1200 (HOR, JSH, JSHH)
|  |  | 9 #14 | [6 empty] | SERVES 36-P-1100 (HOR, FSL, SV, ENABLE)
|  |  | 9 #14 | [6 empty] | SERVES 36-P-1200 (HOR, FSL, SV, ENABLE)
|  |  | 9 #14 | [6 empty] | SERVES 36-P-1300 (HOR, FSL, SV, ENABLE)
E-41 | C32-1100B | 1.5" | 5 #14 | CONTROL | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SERVES 32-ME-1100 (HOR, JSH, JSHH)
|  |  | 5 #14 | [6 empty] | SERVES 32-ME-1200 (HOR, JSH, JSHH)
|  |  | 9 #14 | [6 empty] | SERVES 36-P-1100 (HOR, FSL, SV, ENABLE)
|  |  | 9 #14 | [6 empty] | SERVES 36-P-1200 (HOR, FSL, SV, ENABLE)
|  |  | 9 #14 | [6 empty] | SERVES 36-P-1300 (HOR, FSL, SV, ENABLE)
E-41 | C32-1100C | 1" | 5 #14 | CONTROL | PVC GRS | PVC 40 | P-VLT26 | JB-32-1100 | DB-16 | SERVES 32-ME-1100 (HOR, JSH, JSHH)
|  |  | 5 #14 | [6 empty] | SERVES 32-ME-1200 (HOR, JSH, JSHH)
E-41 | C32-1100D | 3/4" | 5 #14 | CONTROL | PVC GRS | PVC 40 | JB-32-1100 | LCP-32-ME-1100
E-41 | C32-1100E | 3/4" | 3 #14 | CONTROL | PVC GRS | PVC 40 | LCP-32-ME-1100 | 32-JSH/JSHH-1100
E-41 | C32-1200A | 1" | 5#14 | CONTROL | PVC GRS | PVC 40 | JB-32-1100 | JB-32-1200 | DB-17 | SERVES 32-ME-1200 (HOR, JSH, JSHH)
E-41 | C32-1200B | 3/4" | 5#14 | CONTROL | PVC GRS | PVC 40 | JB-32-1200 | LCP-32-ME-1200
E-41 | C32-1200C | 3/4" | 3 #14 | CONTROL | PVC GRS | PVC 40 | LCP-32-ME-1200 | 32-JSH/JSHH-1200
E-41 | C36-1100A | 1.5" | 13 #14 | CONTROL | PVC GRS | PVC 40 | P-VLT26 | P-VLT27 | DB-15 | SERVES 36-P-1100 (HOR, FSL, SV, ENABLE) + SEAL WATER SOLENOID AND LOW FLOW SWITCH
|  |  | 13 #14 | [6 empty] | SERVES 36-P-1200 (HOR, FSL, SV, ENABLE) + SEAL WATER SOLENOID AND LOW FLOW SWITCH
|  |  | 13 #14 | [6 empty] | SERVES 36-P-1300 (HOR, FSL, SV, ENABLE) + SEAL WATER SOLENOID AND LOW FLOW SWITCH
|  |  | 4 #14 | [6 empty] | CONTRACTOR TO VERIFY EXISTING ROUTE (V#19P --> V#20P --> V#21P; USES SP3-6 TO V#20P THEN SP3-6 TO V#21P THEN P9A1 TO VALVE LOCATION); SERVES 51-G-1210
4 #14
E-41 | C36-1100B | 1" | 13 #14 | CONTROL | PVC GRS | PVC 40 | P-VLT27 | LCP-36-P-1100 | DB-36 | SERVES 36-P-1100 (HOR, FSL, SV, ENABLE)
E-41 | C36-1100C | 1" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-36-P-1100 | DS-36-P-1100 |  | SERVES 36-P-1100 (ENABLE)
E-41 | C36-1100D | 1" | 4 #14 | CONTROL | PVC GRS | PVC 40 | LCP-36-P-1100 | 36-SV-1100/36-FSL-1100 |  | SERVES 36-P-1100 SEAL WATER SOLENOID AND LOW FLOW SWITCH
E-41 | C36-1200A | 1" | 13 #14 | CONTROL | PVC GRS | PVC 40 | P-VLT27 | LCP-36-P-1200 | DB-36 | SERVES 36-P-1200 (HOR, FSL, SV, ENABLE)
E-41 | C36-1200B | 1" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-36-P-1200 | DS-36-P-1200 |  | SERVES 36-P-1200 (ENABLE)
E-41 | C36-1200C | 1" | 4 #14 | CONTROL | PVC GRS | PVC 40 | LCP-36-P-1200 | 36-SV-1200/36-FSL-1200 |  | SERVES 36-P-1200 SEAL WATER SOLENOID AND LOW FLOW SWITCH
E-41 | C36-1300A | 1" | 13 #14 | CONTROL | PVC GRS | PVC 40 | P-VLT27 | LCP-36-P-1300 | DB-36 | SERVES 36-P-1300 (HOR, FSL, SV, ENABLE)
E-41 | C36-1300B | 1" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-36-P-1300 | DS-36-P-1300 |  | SERVES 36-P-1300 (ENABLE)
E-41 | C36-1300C | 1" | 4 #14 | CONTROL | PVC GRS | PVC 40 | LCP-36-P-1300 | 36-SV-1300/36-FSL-1300 |  | SERVES 36-P-1300 SEAL WATER SOLENOID AND LOW FLOW SWITCH
E-41 | C36-1400A | 1.5" | 4 #14 | CONTROL | PVC GRS | PVC 40 | PLC-AB | P-VLT25 | DB-4 | SERVES 36-V-1400 (OPEN/CLOSE COMMAND)
|  |  | 4 #14 | [6 empty] | SERVES 36-V-1410 (OPEN/CLOSE COMMAND)
|  |  | 4 #14 | [6 empty] | SERVES 41-G-2110 (OPEN/CLOSE COMMAND)
|  |  | 4 #14 | [6 empty] | SERVES 41-G-2220 (OPEN/CLOSE COMMAND)
|  |  | 4 #14 | [6 empty] | SERVES 51-V-2510 (OPEN/CLOSE COMMAND)
|  |  | 4 #14 | [6 empty] | SERVES 51-V-2530 (OPEN/CLOSE COMMAND)
|  |  | 4 #14 | [6 empty] | SERVES 51-SG-1200 (OPEN/CLOSE COMMAND)
E-41 | C36-1400B | 1.5" | 4 #14 | CONTROL | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SERVES 36-V-1400 (OPEN/CLOSE COMMAND)
|  |  | 4 #14 | [6 empty] | SERVES 36-V-1410 (OPEN/CLOSE COMMAND)
|  |  | 4 #14 | [6 empty] | SERVES 41-G-2110 (OPEN/CLOSE COMMAND)
|  |  | 4 #14 | [6 empty] | SERVES 41-G-2220 (OPEN/CLOSE COMMAND)
|  |  | 4 #14 | [6 empty] | SERVES 51-V-2510 (OPEN/CLOSE COMMAND)
|  |  | 4 #14 | [6 empty] | SERVES 51-V-2530 (OPEN/CLOSE COMMAND)
|  |  | 4 #14 | [6 empty] | SERVES 51-SG-1200 (OPEN/CLOSE COMMAND)
E-41 | C36-1400C | 1" | 4 #14 | CONTROL | PVC GRS | PVC 40 | P-VLT26 | P-VTL27 | DB-15 | SERVES 36-V-1400
|  |  | 4 #14 | [6 empty] | SERVES 36-V-1410
|  |  | 4 #14 | [6 empty] | SERVES 51-V-2530 (OPEN/CLOSE COMMAND)
|  |  | 4 #14 | [6 empty] | SERVES 51-SG-1200 (OPEN/CLOSE COMMAND)
E-42 | C36-1400D | 1" | 4 #14 | CONTROL | PVC GRS | PVC 40 | P-VLT27 | 36-V-1400 | DB-36 | SERVES 36-V-1400
E-42 | C36-1410 | 1" | 4 #14 | CONTROL | PVC GRS | PVC 40 | P-VLT27 | 36-V-1410 | DB-36 | SERVES 36-V-1410
E-41 | C44-1310 | 1" | #14 4C TC | CONTROL | GRS | PVC 40 | MCP-UV | 44-G-1310 |  | VIA CABLE TRAY 44-1000
E-41 | C44-1320 | 1" | #14 4C TC | CONTROL | GRS | PVC 40 | MCP-UV | 44-G-1320 |  | VIA CABLE TRAY 44-1000
E-41 | C44-1330 | 1" | #14 4C TC | CONTROL | GRS | PVC 40 | MCP-UV | 44-G-1330 |  | VIA CABLE TRAY 44-1000
E-41 | C44-1340 | 1" | #14 4C TC | CONTROL | GRS | PVC 40 | MCP-UV | 44-G-1340 |  | VIA CABLE TRAY 44-1000
E-41 | C44-1350 | 1" | #14 4C TC | CONTROL | GRS | PVC 40 | PLC-AB | 44-G-1350 |  | VIA CABLE TRAY 44-1000
E-41 | C51-2100 | 3/4" | 4 #14 | CONTROL | PVC GRS | PVC 40 | VFD-51-P-2100 | 51-P-2100 |  | SERVES TSH
E-41 | C51-2200 | 3/4" | 4 #14 | CONTROL | PVC GRS | PVC 40 | VFD-51-P-2200 | 51-P-2200 |  | SERVES TSH
E-41 | C51-2300 | 3/4" | 4 #14 | CONTROL | PVC GRS | PVC 40 | VFD-51-P-2300 | 51-P-2300 |  | SERVES TSH
E-41 | C51-2400 | 3/4" | 4 #14 | CONTROL | PVC GRS | PVC 40 | VFD-51-P-2400 | 51-P-2400 |  | SERVES TSH
E-41 | C51-2100A | 2" | 4 #14 | CONTROL | PVC GRS | PVC 40 | P-VLT27 | JB-51-2000 | DB-18 | SERVES 51-V-2510 (OPEN/CLOSE COMMAND)
|  |  | 4 #14 | [6 empty] | SERVES 51-V-2530 (OPEN/CLOSE COMMAND)
E-41 | C51-2510 | 3/4" | 4 #14 | CONTROL | PVC GRS | PVC 40 | JB-51-2000 | 51-V-2510 |  | OPEN/CLOSE COMMAND
E-41 | C51-2530 | 3/4" | 4 #14 | CONTROL | PVC GRS | PVC 40 | JB-51-2000 | 51-V-2530 |  | FUTURE OPEN/CLOSE COMMAND
E-40 | C52-1001A | 2" | 4 #14 | CONTROL | PVC GRS | PVC 40 | MCC-RW2 | LCP-52-1001 | EXISTING | EXISTING CONDUIT; SERVES LOW LEVEL INTERLOCK
E-40 | C52-1013A | 1" | 8 #14 | CONTROL | PVC GRS | PVC 40 | VFD-52-P-1013 | P-VLT28 | DB-6 | SERVES 52-P-1013 (HOR, LOS, TSH)
|  |  | 8 #14 |  |  |  | VFD-52-P-1014 |  |  | SERVES 52-P-1014 (HOR, LOS, TSH)
E-40 | C52-1013B | 1" | 8 #14 | CONTROL | PVC GRS | PVC 40 | P-VLT28 | LCP-52-1001 | DB-9 | SERVES 52-P-1013 (HOR, LOS, TSH)
|  |  | 8 #14 | [6 empty] | SERVES 52-P-1014 (HOR, LOS, TSH)
E-40 | C52-1013C | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-52-1001 | 52-TSH-1013 |  | EXISTING CONDUIT
E-40 | C52-1014 | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-52-1001 | 52-TSH-1014 |  |  |  | 8888888888
CONTROL CONDUIT | [11 empty] | 99999999999
SHEET | CONDUIT | SIZE | CONDUCTORS | SERVICE | AG MATERIAL | UG MATERIAL | FROM | TO | DUCTBANKS | NOTES
E-40 | C52-1221A | 2" | 6 #14 | CONTROL | PVC GRS | PVC 40 | MCC-RW2 | LCP-52-1221 |  | ADDED TO WIRE ALREADY IN CONDUIT
E-40 | C52-1221B | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-52-1221 | 52-TSH-1221 |  | RE-USE EXISTING WIRE
E-40 | C52-1222 | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-52-1221 | 52-TSH-1222 |  | RE-USE EXISTUNG WIRE
E-40 | C52-1223 | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-52-1221 | 52-TSH-1223
E-40 | C52-1229 | 3/4" | 4 #14 | CONTROL | PVC GRS | PVC 40 | PLC-UV / SCC-UV | 52-V-1229
E-40 | C52-1228 | 3/4" | 4 #14 | CONTROL | PVC GRS | PVC 40 | PLC-UV / SCC-UV | 52-V-1228
E-36 | C61-1100A | 1" | 9 #14 | CONTROL | PVC GRS | PVC 40 | MCC-AB2 | P-VLT25 | DB-4 | SERVES 61-P-1100 (HOR, ENABLE)
E-36 | C61-1100B | 1" | 9 #14 | CONTROL | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SERVES 61-P-1100 (HOR, ENABLE)
E-36 | C61-1100C | 1" | 9 #14 | CONTROL | PVC GRS | PVC 40 | P-VLT26 | LCP-61-P-1100 | DB-15 | SERVES 61-P-1100 (HOR, ENABLE)
E-36 | C61-1100D | 3/4" | 4 #14 | CONTROL | PVC GRS | PVC 40 | LCP-61-P-1100 | DS-23-P-1100
E-36 | C61-1100E | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-61-P-1100 | TSH-61-1100
E-36 | C61-1100F | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-61-P-1100 | PSH-61-1100
E-38 | C61-1200A | 1" | 9 #14 | CONTROL | PVC GRS | PVC 40 | MCC-AB3 | P-VLT25 | DB-4 | SERVES 61-P-1200 (HOR, ENABLE)
E-38 | C61-1200B | 1" | 9 #14 | CONTROL | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SERVES 61-P-1200 (HOR, ENABLE)
E-38 | C61-1200C | 1" | 9 #14 | CONTROL | PVC GRS | PVC 40 | P-VLT26 | LCP-61-P-1200 | DB-15 | SERVES 61-P-1200 (HOR, ENABLE)
E-38 | C61-1200D | 3/4" | 4 #14 | CONTROL | PVC GRS | PVC 40 | LCP-61-P-1200 | DS-61-P-1200
E-38 | C61-1200E | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-61-P-1200 | TSH-61-1200
E-38 | C61-1200F | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-61-P-1200 | PSH-61-1200
E-36 | C61-1300A | 1" | 9 #14 | CONTROL | PVC GRS | PVC 40 | MCC-AB2 | P-VLT25 | DB-4 | SERVES 61-P-1100 (HOR, ENABLE)
E-36 | C61-1300B | 1" | 9 #14 | CONTROL | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SERVES 61-P-1100 (HOR, ENABLE)
E-36 | C61-1300C | 1" | 9 #14 | CONTROL | PVC GRS | PVC 40 | P-VLT26 | LCP-61-P-1300 | DB-15 | SERVES 61-P-1100 (HOR, ENABLE)
E-36 | C61-1300D | 3/4" | 4 #14 | CONTROL | PVC GRS | PVC 40 | LCP-61-P-1300 | DS-23-P-1300
E-36 | C61-1300E | 3/4" | 2 #14 | CONTROL | PVC GRS | PVC 40 | LCP-61-P-1300 | LSL-61-1310
E-43 | C62-2620 | 1" | 3 #14 | CONTROL | PVC GRS | PVC 40 | LCP-62-ME-2100 | 62-SV-2620
E-43 | C62-2130 | 1" | 3 #14 | CONTROL | PVC GRS | PVC 40 | LCP-62-ME-2100 | 62-SV-2130
E-43 | C62-2230 | 1" | 3 #14 | CONTROL | PVC GRS | PVC 40 | LCP-62-ME-2100 | 62-SV-2230
E-42 | C906 | 1" | 4 #14 | CONTROL | PVC GRS | PVC 40 | V#19P --> V#20P --> V#21P | 41-G-2120, 41-G-2110 |  | EXISTING CONDUIT TO BE INTERCEPTED AND ROUTED TO 41-G-2110 (OPEN/CLOSE COMMAND)
|  |  | 4 #14 | [6 empty] | EXISTING CONDUIT TO BE INTERCEPTED AND ROUTED TO 41-G-2120 (OPEN/CLOSE COMMAND)
E-41 | C923 | 1" | 4 #14 | SIGNAL | N/A | N/A | V#21S |  | N/A | EXISTING CONDUIT USED TO 51-G-1210 (REMOTE, OPEN, CLOSE)
|  |  | 4 #14 |  |  |  |  | 51-SG-1200 |  | EXISTING CONDUIT USED TO 51-SG-1200 (REMOTE, OPEN, CLOSE)
N/A | N/A | N/A | 2 #14 | CONTROL | N/A | N/A | MCC-AB1/MCC-AB2/MCC-AB3/MCC-AB4 | PLC-AB |  | ROUTE THROUGH THE WIRE TRENCH | SERVES 23-P-1300 (START/STOP) |  | 3
|  |  | 2 #14 | [7 empty] | SERVES 23-P-1500 (START/STOP) |  | 4
|  |  | 2 #14 | [7 empty] | SERVES 32-ME-1100 (START/STOP) |  | 6
|  |  | 2 #14 | [7 empty] | SERVES 32-ME-1200 (START/STOP)
|  |  | 2 #14 | [7 empty] | SERVES 44-H-1510 (START/STOP)
|  |  | 2 #14 | [7 empty] | SERVES 44-H-1520 (START/STOP)
|  |  | 2 #14 | [7 empty] | SERVES 23-P-2100 (START/STOP)
|  |  | 2 #14 | [7 empty] | SERVES 23-P-2200 (START/STOP)
|  |  | 2 #14 | [7 empty] | SERVES 23-P-2300 (START/STOP)
E-37 | C21 | 1" | 2 #14 | CONTROL | GRS | PVC 40 | MCC-3 | PLC-MCC3 |  |  | SERVES 21-ME-1200 (START/STOP) |  | 3
|  |  | 2 #14 | [7 empty] | SERVES 21-P-1200 (START/STOP) |  | 4
|  |  | 2 #14 | [7 empty] | SERVES 21-P-2200 (START/STOP) |  | 5
|  |  | 2 #14 | [7 empty] | SERVES 21-ME-1300 (START/STOP)
|  |  | 2 #14 | [7 empty] | SERVES 21-P-1300 (START/STOP)
|  |  | 2 #14 | [7 empty] | SERVES 21-P-2300 (START/STOP) | 999999999
SIGNAL CONDUIT | [11 empty] | 10-10-10 | 1
SHEET | CONDUIT | SIZE | CONDUCTORS | SERVICE | AG MATERIAL | UG MATERIAL | FROM | TO | DUCTBANKS | NOTES |  |  | 2
E-36 | S002A | 1" | PULLCORD | SIGNAL | PVC GRS | PVC 40 | ATS | MAIN GENERATOR | DB-3 | FUTURE COMMS
E-36 | S002B | 1" | PULLCORD | SIGNAL | PVC GRS | PVC 40 | ATS | PLC-AB |  | FUTURE COMMS
E-41 | S121A | 1.5" | 5 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | PLC-AB | A-VLT25 | DB-4 | SERVES 2 LEVEL TRANSDUCERS AND A CHLORINE ANALYZER AT MMWD TANK, CHLORINE ANAYLZER AT RWDP PUMPS
E-41 | S121B | 1.5" | 5 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | A-VLT25 | A-VLT26 | DB-14 | SERVES 2 LEVEL TRANSDUCERS AND A CHLORINE ANALYZER AT MMWD TANK
E-41 | S121C | 1.5" | 5 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | A-VLT26 | A-VLT27 | DB-15 | SERVES 2 LEVEL TRANSDUCERS AND A CHLORINE ANALYZER AT MMWD TANK
E-41 | S121D | 1.5" | 5 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | A-VLT27 | A-VLT30 | DB-18/DB-19 | SERVES 2 LEVEL TRANSDUCERS AND A CHLORINE ANALYZER AT MMWD TANK
E-41 | S121E | 1" | 3 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | A-VLT30 | MMWD TANK | EXISTING | SERVES 2 LEVEL TRANSDUCERS AND A CHLORINE ANALYZER AT MMWD TANK
E-42 | S300 | 1" | 8 #14 | SIGNAL | PVC GRS | PVC 40 | EX CONTROL PANEL | PLC-PSP
E-42 | S400 | 1" | 12 #14 | SIGNAL | PVC GRS | PVC 40 | EX MCC | PLC-PRP
E-42 | S906 | 1" | 8 #14 | SIGNAL | PVC GRS | PVC 40 | V#21S | 41-G-2110
E-42 | S908 | 1" | 8 #14 | SIGNAL | PVC GRS | PVC 40 | V#21S | 41-G-2120
E-42 | S21-1000A | 1" | 1 - #18 TSP, 2 # 14 | SIGNAL | PVC GRS | PVC 40 | PLC-PSP | 21-LIT-1000
E-42 | S21-1000B | 1" | MFG CABLE | SIGNAL | PVC GRS | PVC 40 | 21-LIT-1000 | 21-LE-1000
E-37 | S21-1210A | 2" | 4 #14, 2 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | PLC-MCC3 | A-VLT1 | DB-10 | SERVES 21-FCV-1210
|  |  | 4 #14, 2 - #18 TSP | [6 empty] | SERVES 21-FCV-1310
|  |  | 4 #14, 2 - #18 TSP | [6 empty] | SERVES 21-FCV-1410
|  |  | 4 #14, 2 - #18 TSP | [6 empty] | SERVES 22-FCV-2301, 22-PIT-2300
|  |  | 4 #14, 3 - #18 TSP | [6 empty] | SERVES 22-FCV-2302
|  |  | 8 - #18 TSP | [6 empty] | SERVES 21-LIT-1101, 21-LIT1204A, 21-LIT-1204B, 21-LIT-1205A, 21-LIT-1304A, 21-LIT-1304B, 21-LIT-1305A, 21-LIT-1305B
E-37 | S21-1210B | 2" | 4 #14, 2 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | A-VLT1 | J-BOX2 | EXISTING | SERVES 21-FCV-1210
|  |  | 4 #14, 2 - #18 TSP | [6 empty] | SERVES 21-FCV-1310
|  |  | 4 #14, 2 - #18 TSP | [6 empty] | SERVES 21-FCV-1410
|  |  | 4 #14, 2 - #18 TSP | [6 empty] | SERVES 22-FCV-2301, 22-PIT-2300
|  |  | 4 #14, 3 - #18 TSP | [6 empty] | SERVES 22-FCV-2302
|  |  | 8 - #18 TSP | [6 empty] | SERVES 21-LIT-1101, 21-LIT1204A, 21-LIT-1204B, 21-LIT-1205A, 21-LIT-1304A, 21-LIT-1304B, 21-LIT-1305A, 21-LIT-1305B
E-37 | S21-1210C | 2" | 4 #14, 2 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | J-BOX2 | A-VLT4 | EXISTING | SERVES 21-FCV-1210
|  |  | 4 #14, 2 - #18 TSP | [6 empty] | SERVES 21-FCV-1310
|  |  | 4 #14, 2 - #18 TSP | [6 empty] | SERVES 21-FCV-1410
|  |  | 4 #14, 2 - #18 TSP | [6 empty] | SERVES 22-FCV-2301, 22-PIT-2300
|  |  | 4 #14, 3 - #18 TSP | [6 empty] | SERVES 22-FCV-2302
|  |  | 8 - #18 TSP | [6 empty] | SERVES 21-LIT-1101, 21-LIT1204A, 21-LIT-1204B, 21-LIT-1205A, 21-LIT-1304A, 21-LIT-1304B, 21-LIT-1305A, 21-LIT-1305B
E-37 | S21-1210D | 2" | 4 #14, 2 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | A-VLT4 | J-BOX4 | EXISTING | CONTRACTOR TO PULL NEW WIRE TO J-BOX4, INSTALL TERMINAL BLOCKS AND INTERCEPT EXISTING WIRE | SERVES 21-FCV-1210 (INTERCEPT WIRE IN CONDUIT A-5)
|  |  | 4 #14, 2 - #18 TSP | [7 empty] | SERVES 21-FCV-1310 (INTERCEPT WIRE IN CONDUIT A-5)
|  |  | 4 #14, 2 - #18 TSP | [7 empty] | SERVES 21-FCV-1410 (INTERCEPT WIRE IN CONDUIT A-5)
|  |  | 4 #14, 2 - #18 TSP | [7 empty] | SERVES 22-FCV-2301, 22-PIT-2300 (INTERCEPT WIRE IN CONDUIT A-4)
|  |  | 4 #14, 3 - #18 TSP | [7 empty] | SERVES 22-FCV-2302 (INTERCEPT IN CONDUIT A-29)
|  |  | 8 - #18 TSP | [7 empty] | SERVES 21-LIT-1101, 21-LIT1204A, 21-LIT-1204B, 21-LIT-1205A, 21-LIT-1304A, 21-LIT-1304B, 21-LIT-1305A, 21-LIT-1305B
E-37 | S21-1305 | 3/4" | 1 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | J-BOX4 | 21-LIT-1305B
E-37 | S22-2201A | 2" | 4 #14, 3 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | PLC-MCC3 | A-VLT1 | DB-10 | SERVES 22-FCV-2201, 22-PIT-2200
|  |  | 4 #14, 2 - #18 TSP | [6 empty] | SERVES 22-FCV-2202
|  |  | 4 #14, 2 - #18 TSP | [6 empty] | SERVES 51-FCV-1100
|  |  | 1 - #18 TSP | [6 empty] | SERVES 51-LIT-1100
E-37 | S22-2201B | 2" | 4 #14, 3 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | A-VLT1 | J-BOX2 | EXISTING | SERVES 22-FCV-2201, 22-PIT-2200
|  |  | 4 #14, 2 - #18 TSP | [6 empty] | SERVES 22-FCV-2202
|  |  | 4 #14, 2 - #18 TSP | [6 empty] | SERVES 51-FCV-1100
|  |  | 1 - #18 TSP | [6 empty] | SERVES 51-LIT-1100
E-37 | S22-2201C | 2" | 4 #14, 3 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | J-BOX2 | A-VLT4 | EXISTING | SERVES 22-FCV-2201, 22-PIT-2200
|  |  | 4 #14, 2 - #18 TSP | [6 empty] | SERVES 22-FCV-2202
|  |  | 4 #14, 2 - #18 TSP | [6 empty] | SERVES 51-FCV-1100
|  |  | 1 - #18 TSP | [6 empty] | SERVES 51-LIT-1100
E-37 | S22-2201D | 2" | 4 #14, 3 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | A-VLT4 | J-BOX3 | EXISTING | CONTRACTOR TO PULL NEW WIRE TO J-BOX3, INSTALL TERMINAL BLOCKS AND INTERCEPT EXISTING WIRE | SERVES 22-FCV-2201, 22-PIT-2200 (INTERCEPT WIRE IN CONDUIT A-3)
|  |  | 4 #14, 2 - #18 TSP | [7 empty] | SERVES 22-FCV-2202 (INTERCEPT WIRE IN CONDUIT A-28)
|  |  | 4 #14, 2 - #18 TSP | [6 empty] | SERVES 51-FCV-1100
|  |  | 1 - #18 TSP | [6 empty] | SERVES 51-LIT-1100
E-39 | S23-1000A | 3" | 1 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | PLC-AB | A-VLT25 | DB-4 | SERVES 23-LT-1003
|  |  | 1 - #18 TSP | [6 empty] | SERVES 31-PIT-5000
|  |  | 2 - #18 TSP, 2 #14 | [6 empty] | SERVES 33-G-1100 |  |  | 87
|  |  | 2 - #18 TSP, 2 #14 | [6 empty] | SERVES 33-G-1200
|  |  | 2 - #18 TSP, 2 #14 | [6 empty] | SERVES 33-G-1300
|  |  | 1 - #18 TSP | [6 empty] | SERVES 33-LT-1111
|  |  | 1 - #18 TSP | [6 empty] | SERVES 33-LT-1211
|  |  | 1 - #18 TSP | [6 empty] | SERVES 33-LT-1311
|  |  | 8 #14 | [6 empty] | SERVES 36-V-1400
|  |  | 8 #14 | [6 empty] | SERVES 36-V-1410
|  |  | 1 - #18 TSP; 2 #14 | [6 empty] | SERVES 36-FIT-1000
|  |  | 1 - #18 TSP; 2 #14 | [6 empty] | SERVES 51-FIT-1006
|  |  | 1 - #18 TSP; 2 #14 | [6 empty] | SERVES 51-FIT-1007
|  |  | 8 #14 | [6 empty] | SERVES 51-V-2510, 51-V-2530
|  |  | 6 #14 | [6 empty] | SERVES 23-LSL-1004/LSH-1004A/LSH-1004B
|  |  | 1 - #18 TSP | [6 empty] | SERVES 23-LIT-1002
|  |  | 1 - #18 TSP; 2 #14 | [6 empty] | SERVES 23-FIT-1010
|  |  | 1 - #18 TSP; 2 #14 | [6 empty] | SERVES 23-FIT-1020
|  |  | 1 - #18 TSP; 2 #14 | [6 empty] | SERVES 61-LIT-1000/LSL-1000
E-39 | S23-1000B | 2" | 1 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | A-VLT25 | A-VLT26 | DB-14 | SERVES 23-LT-1003
|  |  | 1 - #18 TSP | [6 empty] | SERVES 31-PIT-5000
|  |  | 2 - #18 TSP, 2 #14 | [6 empty] | SERVES 33-G-1100 |  |  | 87
|  |  | 2 - #18 TSP, 2 #14 | [6 empty] | SERVES 33-G-1200
|  |  | 2 - #18 TSP, 2 #14 | [6 empty] | SERVES 33-G-1300
|  |  | 1 - #18 TSP | [6 empty] | SERVES 33-LT-1111
|  |  | 1 - #18 TSP | [6 empty] | SERVES 33-LT-1211
|  |  | 1 - #18 TSP | [6 empty] | SERVES 33-LT-1311
|  |  | 8 #14 | [6 empty] | SERVES 36-V-1400
|  |  | 8 #14 | [6 empty] | SERVES 36-V-1410
|  |  | 1 - #18 TSP; 2 #14 | [6 empty] | SERVES 36-FIT-1000
|  |  | 1 - #18 TSP; 2 #14 | [6 empty] | SERVES 51-FIT-1006
|  |  | 1 - #18 TSP; 2 #14 | [6 empty] | SERVES 51-FIT-1007
|  |  | 8 #14 | [6 empty] | SERVES 51-V-2510, 51-V-2530
|  |  | 6 #14 | [6 empty] | SERVES 23-LSL-1004/LSH-1004A/LSH-1004B
|  |  | 1 - #18 TSP | [6 empty] | SERVES 23-LIT-1002
|  |  | 1 - #18 TSP; 2 #14 | [6 empty] | SERVES 23-FIT-1010
|  |  | 1 - #18 TSP; 2 #14 | [6 empty] | SERVES 23-FIT-1020
|  |  | 1 - #18 TSP; 2 #14 | [6 empty] | SERVES 61-LIT-1000/LSL-1000 |  | 10-10-10
SIGNAL CONDUIT | [11 empty] | 11-11-11 | 1
SHEET | CONDUIT | SIZE | CONDUCTORS | SERVICE | AG MATERIAL | UG MATERIAL | FROM | TO | DUCTBANKS | NOTES |  |  | 2
E-39 | S23-1000C | 2" | 1 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | A-VLT26 | JB-23-1001 |  | SERVES 23-LT-1003
|  |  | 1 - #18 TSP | [6 empty] | SERVES 31-PIT-5000
|  |  | 2 - #18 TSP, 2 #14 | [6 empty] | SERVES 33-G-1100 |  |  | 87
|  |  | 2 - #18 TSP, 2 #14 | [6 empty] | SERVES 33-G-1200
|  |  | 2 - #18 TSP, 2 #14 | [6 empty] | SERVES 33-G-1300
|  |  | 1 - #18 TSP | [6 empty] | SERVES 33-LT-1111
|  |  | 1 - #18 TSP | [6 empty] | SERVES 33-LT-1211
|  |  | 1 - #18 TSP | [6 empty] | SERVES 33-LT-1311
|  |  | 6 #14 | [6 empty] | SERVES 23-LSL-1004/LSH-1004A/LSH-1004B
|  |  | 1 - #18 TSP | [6 empty] | SERVES 23-LIT-1002
|  |  | 1 - #18 TSP; 2 #14 | [6 empty] | SERVES 23-FIT-1010
|  |  | 1 - #18 TSP; 2 #14 | [6 empty] | SERVES 23-FIT-1020
|  |  | 1 - #18 TSP; 2 #14 | [6 empty] | SERVES 61-LIT-1000/LSL-1000
E-39 | S23-1002A | 3/4" | 1 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | JB-23-1001 | 23-LIT-1002
E-39 | S23-1002B | 3/4" | MFG CABLE | SIGNAL | PVC GRS | PVC 40 | 23-LIT-1002 | 23-LE-1002
E-39 | S23-1003 | 3/4" | 1 - #18 TSP; 6 #14 | SIGNAL | PVC GRS | PVC 40 | JB-23-1001 | LT-23-1003, 23-LSL-1004/LSH-1004A/LSH-1004B
E-39 | S23-1010A | 3/4" | 1 - #18 TSP; 2 #14 | SIGNAL | PVC GRS | PVC 40 | JB-23-1001 | 23-FIT-1010
E-39 | S23-1010B | 2-3/4" | MFG CABLE | SIGNAL | PVC GRS | PVC 40 | 23-FIT-1010 | 23-FE-1010
E-39 | S23-1020A | 3/4" | 1 - #18 TSP; 2 #14 | SIGNAL | PVC GRS | PVC 40 | JB-23-1001 | 23-FIT-1020
E-39 | S23-1020B | 2-3/4" | MFG CABLE | SIGNAL | PVC GRS | PVC 40 | 23-FIT-1020 | 23-FE-1020
E-40 | S23-1020C | 1" | 1 - #18 TSP; 8 #14 | SIGNAL | PVC GRS | PVC 40 | PLC-AB | A-VLT28 | DB-6 | 23-LTL/LSL/LSHA/LSHB-1020
|  |  | 1 - #18 TSP | [6 empty] | SERVES 81-PIT-1000
|  |  | 1 - #18 TSP; 2 #14 | [6 empty] | SERVES 81-FIT-1001
E-42 | S23-1020D | 1" | 15 #14 | SIGNAL | PVC GRS | PVC 40 | A-VLT28 | JB-23-2001 | DB-9 | 23-LTL/LSL/LSHA/LSHB-1020
|  |  | 1 - #18 TSP | [6 empty] | SERVES 81-PIT-1000
|  |  | 1 - #18 TSP; 2 #14 | [6 empty] | SERVES 81-FIT-1001
E-42 | S23-1020E | 3/4" | 1 - #18 TSP; 8 #14 | SIGNAL | PVC GRS | PVC 40 | JB-23-2001 | 23-LTL/LSL/LSHA/LSHB-1020
E-40 | S23-1100A | 2" | 5 - #18 TRIPLEX | SIGNAL | PVC GRS | PVC 40 | MCC-AB1/MCC-AB4 | A-VLT25 | DB-4
E-40 | S23-1100B | 2" | 5 - #18 TRIPLEX | SIGNAL | PVC GRS | PVC 40 | A-VLT25 | A-VLT26 | DB-14
E-40 | S23-1100C | 1" | 1 - #18 TRIPLEX | SIGNAL | PVC GRS | PVC 40 | A-VLT26 | LCP-23-P-1100 | DB-15
E-40 | S23-1200 | 1" | 1 - #18 TRIPLEX | SIGNAL | PVC GRS | PVC 40 | A-VLT26 | LCP-23-P-1200 | DB-15
E-40 | S23-1300 | 1" | 1 - #18 TRIPLEX | SIGNAL | PVC GRS | PVC 40 | A-VLT26 | LCP-23-P-1300 | DB-15
E-40 | S23-1400 | 1" | 1 - #18 TRIPLEX | SIGNAL | PVC GRS | PVC 40 | A-VLT26 | LCP-23-P-1400 | DB-15
E-40 | S23-1500 | 1" | 1 - #18 TRIPLEX | SIGNAL | PVC GRS | PVC 40 | A-VLT26 | LCP-23-P-1500 | DB-15
E-39 | S31-1001A | 2" | 4 - #18 TSP ITC | SIGNAL | PVC GRS | PVC 40 | A-VLT25 | JB-31-1001 |  | SERVES 31-AIT-1001/31-AIT-1002, 31-AIT-1010 |  |  | 53
|  |  | 2 - #18 TSP; 2 #14 | [6 empty] | SERVES 31-G-1540 (REMOTE, POSITION IND, POSITION COMMAND) |  |  | 56
|  |  | 4 - #18 TRIPLEX ITC | [6 empty] | SERVES LCP-31-ME-1100, LCP-31-ME-1200, LCP-31-ME-1300, LCP-31-ME-1400 |  |  | 58
E-39 | S31-1001B | 3/4" | 2 - #18 TSP ITC | SIGNAL | PVC GRS | PVC 40 | JB-31-1001 | 31-AIT-1001/31-AIT-1002 |  | VIA CABLE TRAY 31-1000 |  |  | 22
E-39 | S31-1001C | 3/4" | MFG CABLE | SIGNAL | PVC GRS | PVC 40 | 31-AIT-1001, 31-AIT-1002 | 31-AE-1001 |  |  |  |  | 23
E-39 | S31-1002 | 3/4" | MFG CABLE | SIGNAL | PVC GRS | PVC 40 | 31-AIT-1001, 31-AIT-1002 | 31-AE-1002 |  |  |  |  | 24
E-39 | S31-1010A | 3/4" | 1 - #18 TSP ITC | SIGNAL | PVC GRS | PVC 40 | JB-31-1001 | 31-AIT-1010 |  | VIA CABLE TRAY 1001 |  |  | 25
E-39 | S31-1010B | 3/4" | MFG CABLE | SIGNAL | PVC GRS | PVC 40 | 31-AIT-1010 | 31-AE-1010 |  |  |  |  | 26
E-39 | S31-1100A | 3" | 4 - #18 TSP ITC | SIGNAL | PVC GRS | PVC 40 | PLC-AB | A-VLT25 | DB-4 | SERVES 31-AIT-1001/31-AIT-1002, 31-AIT-1010 |  |  | 53
|  |  | 7 - #18 TSP ITC | [6 empty] | SERVES 31-AIT-2010/31-AIT-3010, 31-AIT-2001/31-AIT-2002, 31-AIT-3001/AIT-31-3002 |  |  | 54
|  |  | 4 - #18 TSP ITC | [6 empty] | SERVES 31-AIT-4010, 31-AIT-4001/31-AIT-4002, 31-LT-4010 |  |  | 55
|  |  | 2 - #18 TSP; 2 #14 | [6 empty] | SERVES 31-G-1540 (REMOTE, POSITION IND, POSITION COMMAND) |  |  | 56
|  |  | 2 - #18 TSP; 2 #14 | [6 empty] | SERVES 31-G-2540 (REMOTE, POSITION IND, POSITION COMMAND) |  |  | 56
|  |  | 2 - #18 TSP; 2 #14 | [6 empty] | SERVES 31-G-3540 (REMOTE, POSITION IND, POSITION COMMAND) |  |  | 56
|  |  | 2 - #18 TSP; 2 #14 | [6 empty] | SERVES 31-G-4540 (REMOTE, POSITION IND, POSITION COMMAND) |  |  | 56
|  |  | 2 - #18 TSP; 2 #14 | [6 empty] | SERVES 31-G-4550 (REMOTE, POSITION IND, POSITION COMMAND) |  |  | 56
|  |  | 2 - #18 TSP; 2 #14 | [6 empty] | SERVES 31-G-4560 (REMOTE, POSITION IND, POSITION COMMAND) |  |  | 57
|  |  | 4 - #18 TRIPLEX ITC |  |  |  | MCC-AB2 |  |  | SERVES LCP-31-ME-1100, LCP-31-ME-1200, LCP-31-ME-1300, LCP-31-ME-1400 |  |  | 58
|  |  | 4 - #18 TRIPLEX ITC | [6 empty] | SERVES LCP-31-ME-2100, LCP-31-ME-2200, LCP-31-ME-2300, LCP-31-ME-2400 |  |  | 59
|  |  | 4 - #18 TRIPLEX ITC |  |  |  | MCC-AB3 |  |  | SERVES LCP-31-ME-3100, LCP-31-ME-3200, LCP-31-ME-3300, LCP-31-ME-3400 |  |  | 60
|  |  | 4 - #18 TRIPLEX ITC | [6 empty] | SERVES LCP-31-ME-4200, LCP-31-ME-4200, LCP-31-ME-4300, LCP-31-ME-4400 |  |  | 61
E-36 | S31-1100B | 3/4" | 1 - #18 TRIPLEX ITC | SIGNAL | PVC GRS | PVC 40 | JB-31-1001 | LCP-31-ME-1100 |  | VIA CABLE TRAY 31-1000 |  |  | 27
E-36 | S31-1200 | 3/4" | 1 - #18 TRIPLEX ITC | SIGNAL | PVC GRS | PVC 40 | JB-31-1001 | LCP-31-ME-1200 |  | VIA CABLE TRAY 31-1000 |  |  | 28
E-36 | S31-1300 | 3/4" | 1 - #18 TRIPLEX ITC | SIGNAL | PVC GRS | PVC 40 | JB-31-1001 | LCP-31-ME-1300 |  | VIA CABLE TRAY 31-1000 |  |  | 29
E-36 | S31-1400 | 3/4" | 1 - #18 TRIPLEX ITC | SIGNAL | PVC GRS | PVC 40 | JB-31-1001 | LCP-31-ME-1400 |  | VIA CABLE TRAY 31-1000 |  |  | 30
E-39 | S31-2001A | 3" | 4 - #18 TSP ITC | SIGNAL | PVC GRS | PVC 40 | A-VLT25 | JB-31-2001 | DB-14 | SERVES 31-AIT-2001/31-AIT-2002, 31-AIT-2010, 31-LT-2010 |  |  | 53
|  |  | 4 - #18 TSP ITC | [6 empty] | SERVES 31-AIT-3001/31-AIT-3002, 31-AIT-3010, 31-LT-3010 |  |  | 53
|  |  | 2 - #18 TSP; 2 #14 | [6 empty] | SERVES 31-G-2540 (REMOTE, POSITION IND, POSITION COMMAND) |  |  | 56
|  |  | 2 - #18 TSP; 2 #14 | [6 empty] | SERVES 31-G-3540 (REMOTE, POSITION IND, POSITION COMMAND) |  |  | 56
|  |  | 4 - #18 TRIPLEX ITC | [6 empty] | SERVES LCP-31-ME-2100, LCP-31-ME-2200, LCP-31-ME-2300, LCP-31-ME-2400 |  |  | 58
|  |  | 4 - #18 TRIPLEX ITC | [6 empty] | SERVES LCP-31-ME-3100, LCP-31-ME-3200, LCP-31-ME-3300, LCP-31-ME-3400 |  |  | 58
E-39 | S31-2001B | 3/4" | 2 - #18 TSP ITC | SIGNAL | PVC GRS | PVC 40 | JB-31-2001 | 31-AIT-2001/31-AIT-2002 |  | VIA CABLE TRAY 31-2000 |  |  | 31
E-39 | S31-2001C | 3/4" | MFG CABLE | SIGNAL | PVC GRS | PVC 40 | 31-AIT-1001/31-AIT-1002 | 31-AE-2001 |  |  |  |  | 32
E-39 | S31-2002 | 3/4" | MFG CABLE | SIGNAL | PVC GRS | PVC 40 | 31-AIT-1001/31-AIT-1002 | 31-AE-2002 |  |  |  |  | 33
E-39 | S31-2010A | 3/4" | 2 - #18 TSP ITC | SIGNAL | PVC GRS | PVC 40 | JB-31-2001 | 31-AIT-2010/31-AIT-3010 |  | VIA CABLE TRAY 2001 |  |  | 34
E-39 | S31-2010B | 3/4" | MFG CABLE | SIGNAL | PVC GRS | PVC 40 | 31-AIT-2010/31-AIT-3010 | 31-AE-2010 |  |  |  |  | 35
E-36 | S31-2100 | 3/4" | 1 - #18 TRIPLEX ITC | SIGNAL | PVC GRS | PVC 40 | JB-31-2001 | LCP-31-ME-2100 |  | VIA CABLE TRAY 31-2000 |  |  | 36
E-36 | S31-2200 | 3/4" | 1 - #18 TRIPLEX ITC | SIGNAL | PVC GRS | PVC 40 | JB-31-2001 | LCP-31-ME-2200 |  | VIA CABLE TRAY 31-2000 |  |  | 37
E-36 | S31-2300 | 3/4" | 1 - #18 TRIPLEX ITC | SIGNAL | PVC GRS | PVC 40 | JB-31-2001 | LCP-31-ME-2300 |  | VIA CABLE TRAY 31-2000 |  |  | 38
E-36 | S31-2400 | 3/4" | 1 - #18 TRIPLEX ITC | SIGNAL | PVC GRS | PVC 40 | JB-31-2001 | LCP-31-ME-2400 |  | VIA CABLE TRAY 31-2000 |  |  | 39
E-39 | S31-3001A | 3/4" | 2 - #18 TSP ITC | SIGNAL | PVC GRS | PVC 40 | JB-31-2001 | 31-AIT-3001/31-AIT-3002 |  | VIA CABLE TRAY 31-2000 |  |  | 40
E-39 | S31-3001B | 3/4" | MFG CABLE | SIGNAL | PVC GRS | PVC 40 | 31-AIT-3001/31-AIT-3002 | 31-AE-3001 |  |  |  |  | 41
E-39 | S31-3002 | 3/4" | MFG CABLE | SIGNAL | PVC GRS | PVC 40 | 31-AIT-3001/31-AIT-3002 | 31-AE-3002 |  |  |  |  | 42
E-39 | S31-3010A | 3/4" | MFG CABLE | SIGNAL | PVC GRS | PVC 40 | 31-AIT-2010/31-AIT-3010 | 31-AE-3010 |  |  |  |  | 43
E-39 | S31-3010B | 3/4" | 1 - #18 TSP ITC | SIGNAL | PVC GRS | PVC 40 | JB-31-2001 | 31-LT-3010 |  |  |  |  | 43
E-38 | S31-3100 | 3/4" | 1 - #18 TRIPLEX ITC | SIGNAL | PVC GRS | PVC 40 | JB-31-2001 | LCP-31-ME-3100 |  | VIA CABLE TRAY 31-2000 |  |  | 44
E-38 | S31-3200 | 3/4" | 1 - #18 TRIPLEX ITC | SIGNAL | PVC GRS | PVC 40 | JB-31-2001 | LCP-31-ME-3200 |  | VIA CABLE TRAY 31-2000 |  |  | 45
E-38 | S31-3300 | 3/4" | 1 - #18 TRIPLEX ITC | SIGNAL | PVC GRS | PVC 40 | JB-31-2001 | LCP-31-ME-3300 |  | VIA CABLE TRAY 31-2000 |  |  | 46
E-38 | S31-3400 | 3/4" | 1 - #18 TRIPLEX ITC | SIGNAL | PVC GRS | PVC 40 | JB-31-2001 | LCP-31-ME-3400 |  | VIA CABLE TRAY 31-2000 |  |  | 47
E-39 | S31-4001A | 3/4" | 2 - #18 TSP ITC | SIGNAL | PVC GRS | PVC 40 | JB-31-4001 | 31-AIT-4001/31-AIT-4002 |  | VIA CABLE TRAY 31-4000 |  |  | 48
E-39 | S31-4001B | 3/4" | MFG CABLE | SIGNAL | PVC GRS | PVC 40 | 31-AIT-4001/31-AIT-4002 | 31-AE-4101 |  |  |  |  | 49
E-39 | S31-4002 | 3/4" | MFG CABLE | SIGNAL | PVC GRS | PVC 40 | 31-AIT-4001/31-AIT-4002 | 31-AE-4102 |  |  |  |  | 50
E-39 | S31-4010A | 3/4" | #18 TSP ITC | SIGNAL | PVC GRS | PVC 40 | JB-31-4001 | 31-AIT-4010 |  | VIA CABLE TRAY 31-4001 |  |  | 51
E-39 | S31-4010B | 3/4" | MFG CABLE | SIGNAL | PVC GRS | PVC 40 | 31-AIT-4010 | 31-AE-4110 |  |  |  | 11-11-11 | 52
SIGNAL CONDUIT | [11 empty] | 12-12-12
SHEET | CONDUIT | SIZE | CONDUCTORS | SERVICE | AG MATERIAL | UG MATERIAL | FROM | TO | DUCTBANKS | NOTES
E-39 | S31-4100A | 2" | 2 - #18 TSP; 2 #14 | SIGNAL | PVC GRS | PVC 40 | A-VLT25 | A-VLT26 | DB-14 | SERVES 31-G-4550 (REMOTE, POSITION IND, POSITION COMMAND) |  |  | 70
|  |  | 2 - #18 TSP; 2 #14 | [6 empty] | SERVES 31-G-4560 (REMOTE, POSITION IND, POSITION COMMAND) |  |  | 71
|  |  | 2 - #18 TSP ITC | [6 empty] | SERVES 31-AIT-4001/31-AIT-4002 |  |  | 72
|  |  | 2 - #18 TSP ITC | [6 empty] | SERVES 31-AIT-4010 |  |  | 73
|  |  | 2 - #18 TSP; 2 #14 | [6 empty] | SERVES 31-G-4550 (REMOTE, POSITION IND, POSITION COMMAND) |  |  | 56
|  |  | 2 - #18 TSP; 2 #14 | [6 empty] | SERVES 31-G-4560 (REMOTE, POSITION IND, POSITION COMMAND) |  |  | 57
|  |  | 2 - #18 TSP; 2 #14 | [6 empty] | SERVES 31-G-4540 (REMOTE, POSITION IND, POSITION COMMAND) |  |  | 56
|  |  | 4 - #18 TRIPLEX ITC | [6 empty] | SERVES LCP-31-ME-4200, LCP-31-ME-4200, LCP-31-ME-4300, LCP-31-ME-4400 |  |  | 74
E-39 | S31-4100B | 2" | 2 - #18 TSP; 2 #14 | SIGNAL | PVC GRS | PVC 40 | A-VLT26 | JB-31-4001 |  | SERVES 31-G-4550 (REMOTE, POSITION IND, POSITION COMMAND) |  |  | 70
|  |  | 2 - #18 TSP; 2 #14 | [6 empty] | SERVES 31-G-4560 (REMOTE, POSITION IND, POSITION COMMAND) |  |  | 71
|  |  | 2 - #18 TSP ITC | [6 empty] | SERVES 31-AIT-4001/31-AIT-4002 |  |  | 72
|  |  | 2 - #18 TSP ITC | [6 empty] | SERVES 31-AIT-4010 |  |  | 73
|  |  | 2 - #18 TSP; 2 #14 | [6 empty] | SERVES 31-G-4550 (REMOTE, POSITION IND, POSITION COMMAND) |  |  | 56
|  |  | 2 - #18 TSP; 2 #14 | [6 empty] | SERVES 31-G-4560 (REMOTE, POSITION IND, POSITION COMMAND) |  |  | 57
|  |  | 2 - #18 TSP; 2 #14 | [6 empty] | SERVES 31-G-4540 (REMOTE, POSITION IND, POSITION COMMAND) |  |  | 56
|  |  | 4 - #18 TRIPLEX ITC | [6 empty] | SERVES LCP-31-ME-4200, LCP-31-ME-4200, LCP-31-ME-4300, LCP-31-ME-4400 |  |  | 74
E-38 | S31-4100C | 3/4" | 1 - #18 TRIPLEX ITC | SIGNAL | PVC GRS | PVC 40 | JB-31-4001 | LCP-31-ME-4200 |  | VIA CABLE TRAY 31-4000 |  |  | 75
E-38 | S31-4200 | 3/4" | 1 - #18 TRIPLEX ITC | SIGNAL | PVC GRS | PVC 40 | JB-31-4001 | LCP-31-ME-4200 |  | VIA CABLE TRAY 31-4000 |  |  | 76
E-38 | S31-4300 | 3/4" | 1 - #18 TRIPLEX ITC | SIGNAL | PVC GRS | PVC 40 | JB-31-4001 | LCP-31-ME-4300 |  | VIA CABLE TRAY 31-4000 |  |  | 77
E-38 | S31-4400 | 3/4" | 1 - #18 TRIPLEX ITC | SIGNAL | PVC GRS | PVC 40 | JB-31-4001 | LCP-31-ME-4400 |  | VIA CABLE TRAY 31-4000 |  |  | 78
E-38 | S31-4550 | 3/4" | 2 - #18 TSP; 2 #14 | SIGNAL | PVC GRS | PVC 40 | JB-31-4001 | 31-G-4550 |  | REMOTE, POSITION IND, POSITION COMMAND |  |  | 79
E-38 | S31-4560 | 3/4" | 2 - #18 TSP; 2 #14 | SIGNAL | PVC GRS | PVC 40 | JB-31-4001 | 31-G-4560 |  | REMOTE, POSITION IND, POSITION COMMAND |  |  | 80
E-39 | S31-5510A | 1" | PULL CORD | SIGNAL | PVC GRS | PVC 40 | PLC-AB | A-VLT25 | DB-4 | SERVES FUTURE METHANOL PUMP |  |  | 81
E-39 | S31-5510B | 1" | PULL CORD | SIGNAL | PVC GRS | PVC 40 | A-VLT25 | JB-31-2001 | DB-14 | SERVES FUTURE METHANOL PUMP |  |  | 82
E-39 | S31-5510C | 1" | PULL CORD | SIGNAL | PVC GRS | PVC 40 | JB-31-2001 | JB-31-5501 | DB-15 | SERVES FUTURE METHANOL PUMP (VIA CABLE TRAY 31-2000) |  |  | 83
E-39 | S31-5000 | 1" | 1 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | JB-23-1001 | 31-PIT-5000 | DB-15 |  |  |  | 84
E-39 | S33-1100D | 3/4" | 2 - #18 TSP; 2 #14 | SIGNAL | PVC GRS | PVC 40 | JB-23-1001 | 33-G-1100 |  | SERVES 33-G-1100
E-39 | S33-1111 | 3/4" | 1 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | JB-23-1001 | 33-LT-1111
E-39 | S33-1200 | 3/4" | 2 - #18 TSP; 2 #14 | SIGNAL | PVC GRS | PVC 40 | JB-23-1001 | 33-G-1200 |  | SERVES 33-G-1200
E-39 | S33-1211 | 3/4" | 1 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | S33-1111 | 33-LT-1211
E-41` | S36-1000A | 1" | 1 - #18 TSP; 2 #14 | SIGNAL | PVC GRS | PVC 40 | A-VLT26 | A-VLT27 | DB-15 | SERVES 36-FIT-1000
|  |  | 4 #14 | [6 empty] | SERVES 36-V-1400
|  |  | 4 #14 | [6 empty] | SERVES 36-V-1410
E-41 | S36-1000B | 1" | 1 - #18 TSP; 2 #14 | SIGNAL | PVC GRS | PVC 40 | A-VLT27 | 36-FIT-1000 | DB-36
E-41 | S36-1400 | 1" | 4 #14 | SIGNAL | PVC GRS | PVC 40 | A-VLT27 | 36-V-1400 | DB-36
E-41 | S36-1410 | 1" | 4 #14 | SIGNAL | PVC GRS | PVC 40 | A-VLT27 | 36-V-1410 | DB-36
E-42 | S41-1100A | 1" | 1 - #18 TSP; 4 #14 | SIGNAL | PVC GRS | PVC 40 | PLC-AB | V#20S | DB-33 | CONTRACTOR TO VERIFY EXISTING ROUTE (V#20S --> 41-SG-1100; USES S907 TO V#20S AND S920 TO VALVE) AND PULL NEW WIRE; SERVES 41-SG-1100
|  |  | 8 #14 | [6 empty] | CONTRACTOR TO VERIFY EXISTING ROUTE (V#20S --> V#21S --> 51-G-1210; USES S907 TO V#20S/V#21S AND P923 TO VALVE); SERVES 51-G-1210
|  |  | 8 #14 | [6 empty] | CONTRACTOR TO VERIFY EXISTING ROUTE (V#20S --> V#21S --> 51-G-1210; USES S907 TO V#20S/V#21S AND S906 AND S907 TO VALVE); SERVES 41-G-2110 & SERVES 41-G-2120 IT IS ANTICIPATED THE CONDUIT WILL BE INTERCEPTED AND NEED TO BE REROUTED ABOVE GROUND
E-42 | S42-1120 | 1" | 1 - #18 TSP; 2 #14 | SIGNAL | PVC GRS | PVC 40 | PLC-AB | 42-FIT-1120 |  | VIA TRENCH
E-43 | S43-1000A | 1.5" | 6 - #18 TSP; 2 #14 | SIGNAL | PVC GRS | PVC 40 | PLC-AB | A-VLT28 | DB-6 | SERVES 43-AIT-1300, 43-AIT-1310, 43-AIT-1320, LIT-43-1011, LIT-1012
|  |  | 4 - #18 TSP; 10 #14 | [6 empty] | SERVES 43-P-1100, 43-P-1200
|  |  | 4 #14 | [6 empty] | SERVES 43-FSL-1400
E-43 | S43-1000B | 1.5" | 6 - #18 TSP; 2 #14 | SIGNAL | PVC GRS | PVC 40 | A-VLT28 | JB-43-1001 | DB-7 | SERVES 43-AIT-1300, 43-AIT-1310, 43-AIT-1320, LIT-43-1011, LIT-1012
|  |  | 4 - #18 TSP; 10 #14 | [6 empty] | SERVES 43-P-1100, 43-P-1200
|  |  | 4 #14 | [6 empty] | SERVES 43-FSL-1400
E-43 | S43-1011 | 3/4" | 1 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | JB-43-1001 | 43-LIT-1011 |  | VIA TRENCH
E-43 | S43-1012 | 3/4" | 1 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | JB-43-1001 | 43-LIT-1012 |  | VIA TRENCH
E-43 | S43-1100 | 1" | 2 - #18 TSP; 5 #14 | SIGNAL | PVC GRS | PVC 40 | JB-43-1001 | 43-P-1100 |  | VIA TRENCH
E-43 | S43-1200 | 1" | 2 - #18 TSP; 5 #14 | SIGNAL | PVC GRS | PVC 40 | JB-43-1001 | 43-P-1200 |  | VIA TRENCH
E-43 | S43-1300 | 3/4" | 1 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | JB-43-1001 | 43-AIT-1300 |  | VIA TRENCH
E-43 | S43-1310 | 3/4" | 1 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | JB-43-1001 | 43-AIT-1310 |  | VIA TRENCH
E-43 | S43-1320 | 3/4" | 1 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | JB-43-1001 | 43-AIT-1320 |  | VIA TRENCH
E-42 | S43-1400 | 3/4" | 4 #14 | SIGNAL | PVC GRS | PVC 40 | JB-43-1001 | 43-FSH-1400 |  | VIA TRENCH
E-42 | S44-1000A | 1" | 1 - #18 TSP; 2 #14 | SIGNAL | PVC GRS | PVC 40 | PLC-AB | 44-FIT-1000 |  | VIA TRENCH
E-42 | S44-1000B | 2" | MFG CABLE; 3 #14 | SIGNAL | PVC GRS | PVC 40 | 44-FIT-1000 | V#20S | DB-33 | SERVES 42-FIT-1120; 42-LSH-1120
E-42 | S44-1000C | 1" | MFG CABLE | SIGNAL | PVC GRS | PVC 40 | V#20S | 44-FE-1000 | DB-21 | SERVES 42-FIT-1120
E-42 | S44-1000D | 1" | 3 #14 | SIGNAL | PVC GRS | PVC 40 | V#20S | 44-LSH-1000
E-41 | S44-1010 | 1" | 1 - #18 TSP; 2 #14 | SIGNAL | PVC GRS | PVC 40 | MCP-UV | 44-AIT-1010 |  | VIA TRENCH
E-41 | S44-1100A | 1" | 3 #14 | SIGNAL | PVC GRS | PVC 40 | MCP-UV | 44-LSL-1100
E-41 | S44-1100B | 1.5" | MFG CABLE | SIGNAL | PVC GRS | PVC 40 | MCP-UV | PSU-UV-1
E-41 | S44-1200A | 1" | 3 #14 | SIGNAL | PVC GRS | PVC 40 | MCP-UV | 44-LSL-1200
E-41 | S44-1200B | 1.5" | MFG CABLE | SIGNAL | PVC GRS | PVC 40 | MCP-UV | PSU-UV-2
E-41 | S44-1310 | 1" | #14 4C TC | SIGNAL | GRS | PVC 40 | MCP-UV | 44-G-1310 | DB-5 | VIA CABLE TRAY 44-1000
E-41 | S44-1320 | 1" | #14 4C TC | SIGNAL | GRS | PVC 40 | MCP-UV | 44-G-1320 | DB-5 | VIA CABLE TRAY 44-1000
E-41 | S44-1330 | 1" | #14 4C TC | SIGNAL | GRS | PVC 40 | MCP-UV | 44-G-1330 | DB-5 | VIA CABLE TRAY 44-1000
E-41 | S44-1340 | 1" | #14 4C TC | SIGNAL | GRS | PVC 40 | MCP-UV | 44-G-1340 | DB-5 | VIA CABLE TRAY 44-1000
E-41 | S44-1350 | 1" | #14 4C TC 2 - #18 TSP ITC | SIGNAL | GRS | PVC 40 | PLC-AB | 44-G-1350 | DB-5 | VIA CABLE TRAY 44-1000
E-41 | S44-1500 | 3/4" | 2 #14 | SIGNAL | GRS | PVC 40 | PLC-AB | 44-FSH-1500 | DB-5
E-36 | S44-1530 | 3/4" | 2 - #18 TSP | SIGNAL | GRS | PVC 40 | PLC-AB | 44-TT-1530 / 44-AE-1540 | DB-5
E-36 | S44-1550 | 3/4" | 2 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | PLC-AB | 44-TT-1550 / 44-AE-1560 | DB-5
E-41 | S44-1900 | 1" | 2 - #18 TSP, 2 #14 | SIGNAL | PVC GRS | PVC 40 | PLC-AB | 44-FIT-1920/44-FE-1920 | DB-5 | UV DECLORINATION SYSTEM CHLORINE ANALYZERS
|  |  | 2 - #18 TSP; 4 #14 |  |  |  |  | 44-P-1900 |  | REMOTE, RUN, FAIL, SPEED IND, SPEED COMMAND
E-41 | S51-1000A | 2" | 5 - #18 TSP; 18 #14 | SIGNAL | PVC GRS | PVC 40 | A-VLT26 | A-VLT27 | DB-15 | SERVES 51-FIT-1006, 51-FIT-1007, 51-PIT-1009, 51-PIT-1010, 51-V-2510, 51-V-2530
E-41 | S51-1000B | 2" | 5 - #18 TSP; 18 #14 | SIGNAL | PVC GRS | PVC 40 | A-VLT27 | JB-51-2001 | DB-18 | SERVES 51-FIT-1006, 51-FIT-1007, 51-PIT-1009, 51-PIT-1010, 51-V-2510, 51-V-2530
E-41 | S51-1006 | 3/4" | 1 - #18 TSP; 2 #14 | SIGNAL | PVC GRS | PVC 40 | JB-51-2001 | 51-FIT-1006
E-41 | S51-1007 | 3/4" | 1 - #18 TSP; 2 #14 | SIGNAL | PVC GRS | PVC 40 | JB-51-2001 | 51-FIT-1007
E-41 | S51-1009 | 3/4" | 1 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | JB-51-2001 | 51-PIT-1009
E-41 | S51-1010 | 3/4" | 1 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | JB-51-2001 | 51-PIT-1010
E-42 | S51-1009A | 1" | 1 - #18 TSP; 2 #14 | SIGNAL | PVC GRS | PVC 40 | PLC-AB | 51-FIT-1009 |  | VIA TRENCH
E-42 | S51-1009B | 2" | MFG CABLE; 3 #14 | SIGNAL | PVC GRS | PVC 40 | 51-FIT-1009 | V#20S | DB-33 | SERVES 42-FIT-1120; 42-LSH-1120
E-42 | S51-1009C | 1" | MFG CABLE | SIGNAL | PVC GRS | PVC 40 | V#20S | 51-FE-1009 | DB-21 | SERVES 42-FIT-1120
E-37 | S51-1101A | 1" | 4 #14, 2 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | A-VLT2 | 51-FCV-1101 | EXISTING | CONTRACTOR TO INSTALL NEW CONDUIT AND PULL NEW WIRE TO EXISTING VALVE
E-37 | S51-1101B | 1" | 1 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | A-VLT2 | 51-LIT-1101 | EXISTING | CONTRACTOR TO INSTALL NEW CONDUIT AND PULL NEW WIRE TO EXISTING LEVEL TRANSMITTER
E-41 | S51-2510 | 3/4" | 4 #14 | SIGNAL | PVC GRS | PVC 40 | JB-51-2001 | 51-V-2510 |  | REMOTE, OPEN/CLOSED INDICATION
E-41 | S51-2530 | 3/4" | 4 #14 | SIGNAL | PVC GRS | PVC 40 | JB-51-2001 | 51-V-2530 |  | FUTURE REMOTE, OPEN/CLOSED INDICATION |  | 12-12-12
SIGNAL CONDUIT | [11 empty] | 13-13-13 | 1
SHEET | CONDUIT | SIZE | CONDUCTORS | SERVICE | AG MATERIAL | UG MATERIAL | FROM | TO | DUCTBANKS | NOTES |  |  | 2
E-40 | S52-1013A | 1" | 1 - SHD TRIPLEX | SIGNAL | PVC GRS | PVC 40 | VFD-52-P-1013 | A-VLT28 | DB-6 | SERVES 52-P-1014 (POT)
E-40 | S52-1013B | 1" | 1 - SHD TRIPLEX | SIGNAL | PVC GRS | PVC 40 | A-VLT28 | LCP-52-1001 | DB-9 | SERVES 52-P-1013 (POT)
|  |  | 1 - SHD TRIPLEX | [6 empty] | SERVES 52-P-1014 (POT)
E-40 | S52-1014 | 1" | 1 - SHD TRIPLEX | SIGNAL | PVC GRS | PVC 40 | VFD-52-P-1014 | A-VLT28 | DB-6 | SERVES 52-P-1014 (POT)
E-40 | S52-1220 | EX | 2 - #18 TSP 2 #14 | SIGNAL | PVC GRS | PVC 40 | LCP-52-1221 | PLC-RW
E-40 | S52-1225 | 3/4" | 1 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | LCP-52-1221 | PIT-1225
E-40 | S52-1229 | 3/4" | MFG CABLES | SIGNAL | PVC GRS | PVC 40 | LCP-52-1221 | FE-1227
E-40 | S52-1229 | 3/4" | 4 #14 | SIGNAL | PVC GRS | PVC 40 | PLC-UV / SCC-UV | 52-V-1229
E-40 | S52-1228 | 3/4" | 4 #14 | SIGNAL | PVC GRS | PVC 40 | PLC-UV / SCC-UV | 52-V-1228
E-40 | S52-1200 | 3/4" | 1 - #18 TSP; 2 #14 | SIGNAL | PVC GRS | PVC 40 | PLC-RWTF | 52-AIT-1200
E-40 | S52-1250 | 3/4" | 1 - #18 TSP; 2 #14 | SIGNAL | PVC GRS | PVC 40 | PLC-RWTF | 52-AIT-1250
E-39 | S61-1000A | 3/4" | 1 - #18 TSP; 2 #14 | SIGNAL | PVC GRS | PVC 40 | JB-23-1001 | 61-LIT-1000
E-39 | S61-1000B | 3/4" | MFG CABLE | SIGNAL | PVC GRS | PVC 40 | 61-LIT-1000 | 61-LE-1000
E-39 | S61-1000B | 3/4" | 3 #14 | SIGNAL | PVC GRS | PVC 40 | JB-23-1001 | 61-LSL-1000
E-43 | S62-1100 | 1" | MFG CABLE | SIGNAL | PVC GRS | PVC 40 | LCP-62-ME-2100 | 62-LE-1100
E-43 | S62-2610 | 1" | 4 #14 | SIGNAL | PVC GRS | PVC 40 | LCP-62-ME-2100 | 62-PDSL-2610
E-43 | S62-2620A | 1" | MFG CABLE | SIGNAL | PVC GRS | PVC 40 | LCP-62-ME-2100 | 62-FE-2620
E-43 | S62-2620B | 1" | 1 - #18 TSP; 2 #14 | SIGNAL | PVC GRS | PVC 40 | PLC-MCC3 | 62-FIT-2620
E-43 | S62-2620C | 1" | MFG CABLE | SIGNAL | PVC GRS | PVC 40 | 62-FIT-2620 | 62-FE-2620
E-43 | S62-2640A | 1" | 1 - #18 TSP; 2 #14 | SIGNAL | PVC GRS | PVC 40 | PLC-MCC3 | 62-FIT-2640
E-43 | S62-2640B | 1" | MFG CABLE | SIGNAL | PVC GRS | PVC 40 | 62-FIT-2640 | 62-FE-2640
E-43 | S62-5010 | 1" | 3 #14 | SIGNAL | PVC GRS | PVC 40 | PLC-MCC3 | 62-FSH-5010
E-43 | S62-2100 | 1" | 3 #14 | SIGNAL | PVC GRS | PVC 40 | LCP-62-ME-2100 | 62-LS-2100
E-43 | S62-2200 | 1" | 3 #14 | SIGNAL | PVC GRS | PVC 40 | LCP-62-ME-2100 | 62-LS-2200
E-43 | S62-2400 | 1" | 1 - #18 TSP | SIGNAL | PVC GRS | PVC 40 | LCP-62-ME-2100 | 62-LT-2400
E-43 | S62-2300A | 1" | 3 #14 | SIGNAL | PVC GRS | PVC 40 | LCP-62-ME-2100 | 62-TSH-2300
E-43 | S62-2300B | 1" | 3 #14 | SIGNAL | PVC GRS | PVC 40 | LCP-62-ME-2100 | 62-PSH-2300
E-43 | S62-2500 | 1" | 1 - #18 TSP; 2 #14 | SIGNAL | PVC GRS | PVC 40 | LCP-62-ME-2100 | 62-FIT-2500
E-37 | S21 | 1.5" |  | SIGNAL | GRS | PVC 40 | MCC-3 |  |  | ROUTE THROUGH THE WIRE TRENCH |  |  | 3
|  |  | 5 #14 |  |  |  |  | PLC-MCC3 |  |  | SERVES 21-ME-1200 (REMOTE, RUN, HIGH TORQUE, HI-HI TORQUE) |  | 5
|  |  | 4 #14 | [7 empty] | SERVES 22-P-1200 (REMOTE, RUN, FAIL) |  | 6
|  |  | 4 #14 | [7 empty] | SERVES 22-P-2200 (REMOTE, RUN, FAIL) |  | 7
|  |  | 5 #14 | [7 empty] | SERVES 21-ME-1300 (REMOTE, RUN, HIGH TORQUE, HI-HI TORQUE) |  | 15
|  |  | 4 #14 | [7 empty] | SERVES 22-P-1300 (REMOTE, RUN, FAIL) |  | 16
|  |  | 4 #14 | [7 empty] | SERVES 22-P-2300 (REMOTE, RUN, FAIL) |  | 17
N/A | N/A | N/A |  | SIGNAL | N/A | N/A | MCC-AB2 |  |  | ROUTE THROUGH THE WIRE TRENCH |  |  | 3
|  |  | 4 #14 | [7 empty] | SERVES 23-P-2100 (REMOTE, RUN, FAIL) |  | 12
|  |  | 4 #14 | [7 empty] | SERVES 23-P-2200 (REMOTE, RUN, FAIL) |  | 13
|  |  | 4 #14 | [7 empty] | SERVES 23-P-2300 (REMOTE, RUN, FAIL) |  | 22
E-41 | S104 | 2" | 6 #14 | SIGNAL | GRS | PVC 40 | MCC-AB2/MCC-AB3 | PLC-AB |  | SERVES 32-ME-1100 (REMOTE, RUN, FAIL, HIGH TORQUE, HI-HI TORQUE)
|  |  | 6 #14 | [6 empty] | SERVES 32-ME-1200 (REMOTE, RUN, FAIL, HIGH TORQUE, HI-HI TORQUE)
|  |  | 6 #14 | [6 empty] | SERVES 32-ME-1300 (REMOTE, RUN, FAIL, HIGH TORQUE, HI-HI TORQUE)
|  |  | 4 #14 | [6 empty] | SERVES 33-P-1400 (REMOTE, RUN, FAIL)
|  |  | 4 #14 | [6 empty] | SERVES 44-H-1510 (REMOTE, RUN FAIL)
|  |  | 4 #14 | [6 empty] | SERVES 44-H-1520 (REMOTE, RUN FAIL)
E-42 | S907 | 2" | 1 - #18 TSP; 4 #14 | SIGNAL | N/A | N/A | V#19S | V#20S | N/A | EXISTING CONDUIT USED FOR 41-SG-1100 (REMOTE, POSITION IND, POSITION COMMAND) |  |  | 25
|  |  | 4 #14 | [6 empty] | EXISTING CONDUIT USED FOR 41-SG-1100 (REMOTE, OPEN, CLOSE) |  |  | 26
E-42 |  | 2" | 4 #14 | SIGNAL | N/A | N/A | V#20S | V#21S | N/A | EXISTING CONDUIT USED FOR 41-SG-1100 (REMOTE, OPEN, CLOSE) |  |  | 27
E-42 | S920 | 1" | 1 - #18 TSP; 4 #14 | SIGNAL | N/A | N/A | V#20S | 41-SG-1100 | N/A | EXISTING CONDUIT USED FOR 41-SG-1100 (REMOTE, POSITION IND, POSITION COMMAND) |  | 13-13-13 | 28
SPARE CONDUIT | [11 empty] | 14-14-14 | 1
SHEET | CONDUIT | SIZE | CONDUCTORS | SERVICE | AG MATERIAL | UG MATERIAL | FROM | TO | DUCTBANKS | NOTES |  |  | 2
E-42 | SP064 | 1" | PULL CORD | 120VAC | PVC GRS | PVC 40 | P-VLT28 | JB-23-2000 | DB-9 | SPARE |  |  | 36
E-42 | SP067 | 1" | PULL CORD | 480VAC | PVC GRS | PVC 40 | P-VLT28 | JB-23-2000 | DB-9 | SPARE |  |  | 39
E-42 | SP068 | 1" | PULL CORD | SIGNAL | PVC GRS | PVC 40 | A-VLT28 | JB-23-2001 | DB-9 | SPARE |  |  | 40
E-37 | SP21-1000C | EX | PULL CORD | SIGNAL | PVC GRS | PVC 40 | A-VLT3 | J-BOX4 | EXISTING | SPARE |  |  | 45
E-37 | SP21-1001A | EX | PULL CORD | 480VAC | PVC GRS | PVC 40 | MCC-AB2/MCC-AB3 | P-VLT2 | EXISTING | SPARE |  |  | 46
E-37 | SP21-1001B | EX | PULL CORD | 480VAC | PVC GRS | PVC 40 | P-VLT2 | P-VLT3 | EXISTING | SPARE |  |  | 47
E-37 | SP21-1001C | EX | PULL CORD | 480VAC | PVC GRS | PVC 40 | P-VLT3 | J-BOX3 | EXISTING | SPARE |  |  | 48
E-37 | SP21-1002A | EX | PULL CORD | 480VAC | PVC GRS | PVC 40 | DP-AB2 | P-VLT2 | EXISTING | SPARE |  |  | 49
E-37 | SP21-1002B | EX | PULL CORD | 480VAC | PVC GRS | PVC 40 | P-VLT2 | P-VLT3 | EXISTING | SPARE |  |  | 50
E-37 | SP21-1002C | EX | PULL CORD | 480VAC | PVC GRS | PVC 40 | P-VLT3 | J-BOX4 | EXISTING | SPARE |  |  | 51
E-39 | SP23-1000A | 1" | PULL CORD | 480VAC | PVC GRS | PVC 40 | DP-AB2 | P-VLT25 | DB-4 | SPARE |  |  | 55
E-39 | SP23-1000B | 1" | PULL CORD | 120VAC | PVC GRS | PVC 40 | LP-AB | P-VLT25 | DB-4 | SPARE |  |  | 56
E-39 | SP23-1000C | 1" | PULL CORD | CONTROL | PVC GRS | PVC 40 | MCC-AB1/MCC-AB4 | P-VLT25 | DB-4 | SPARE |  |  | 57
E-39 | SP23-1000D | 2" | PULL CORD | SIGNAL | PVC GRS | PVC 40 | PLC-AB | A-VLT25 | DB-4 | SPARE |  |  | 58
E-39 | SP23-1000E | 1" | PULL CORD | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SPARE |  |  | 55
E-39 | SP23-1000F | 1" | PULL CORD | 120VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SPARE |  |  | 56
E-39 | SP23-1000G | 1" | PULL CORD | CONTROL | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SPARE |  |  | 57
E-39 | SP23-1000H | 2" | PULL CORD | SIGNAL | PVC GRS | PVC 40 | A-VLT25 | A-VLT26 | DB-14 | SPARE |  |  | 58
E-38 | SP23-1000I | 1" | PULL CORD | 480VAC | PVC GRS | PVC 40 | P-VLT26 | JB-23-1000 |  | SPARE |  |  | 55
E-39 | SP23-1000J | 1" | PULL CORD | 120VAC | PVC GRS | PVC 40 | P-VLT26 | JB-23-1000 |  | SPARE |  |  | 56
E-40 | SP23-1000K | 1" | PULL CORD | CONTROL | PVC GRS | PVC 40 | P-VLT26 | JB-23-1000 |  | SPARE |  |  | 57
E-39 | SP23-1000L | 2" | PULL CORD | SIGNAL | PVC GRS | PVC 40 | A-VLT26 | JB-23-1001 |  | SPARE |  |  | 58
E-39 | SP31-1000A | 1" | PULL CORD | 120VAC | PVC GRS | PVC 40 | LP-AB | P-VLT25 | DB-4 | SPARE |  |  | 62
E-39 | SP31-1000B | 1" | PULL CORD | 120VAC | PVC GRS | PVC 40 | P-VLT25 | JB-31-1000 |  | SPARE |  |  | 63
E-36 | SP31-1201 | 2" | PULL CORD | 120VAC | PVC GRS | PVC 40 | P-VLT25 | JB-31-2000
E-39 | SP31-2000A | 2" | PULL CORD | 120VAC | PVC GRS | PVC 40 | LP-AB | P-VLT25 | DB-4 | SPARE |  |  | 62
E-39 | SP31-2000B | 2" | PULL CORD | 120VAC | PVC GRS | PVC 40 | P-VLT25 | JB-31-2000 |  | SPARE |  |  | 63
E-39 | SP31-4000A | 1" | PULL CORD | 120VAC | PVC GRS | PVC 40 | LP-AB | P-VLT25 | DB-4 | SPARE |  |  | 62
E-39 | SP31-4000B | 1" | PULL CORD | 120VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SPARE |  |  | 63
E-39 | SP31-4000C | 1" | PULL CORD | 120VAC | PVC GRS | PVC 40 | P-VLT26 | JB-31-4000 |  | SPARE |  |  | 63
E-36 | SP31-1100A | 2" | PULL CORD | 480VAC | PVC GRS | PVC 40 | MCC-AB2 | P-VLT25 | DB-4 | SPARE |  |  | 65
E-36 | SP31-1100B | 2" | PULL CORD | 480VAC | PVC GRS | PVC 40 | P-VLT25 | JB-31-1000 |  | SPARE |  |  | 66
E-36 | SP31-2100A | 2" | PULL CORD | 480VAC | PVC GRS | PVC 40 | MCC-AB2 | P-VLT25 | DB-4 | SPARE |  |  | 65
E-36 | SP31-2100B | 2" | PULL CORD | 480VAC | PVC GRS | PVC 40 | P-VLT25 | JB-31-2000 | DB-14 | SPARE |  |  | 66
E-38 | SP31-4100A | 2" | PULL CORD | 480VAC | PVC GRS | PVC 40 | MCC-AB3 | P-VLT25 | DB-4 | SPARE |  |  | 65
E-38 | SP31-4100B | 2" | PULL CORD | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SPARE |  |  | 66
E-38 | SP31-4100C | 2" | PULL CORD | 480VAC | PVC GRS | PVC 40 | P-VLT26 | JB-31-4000 |  | SPARE |  |  | 66
E-36 | SP31-1101A | 2" | PULL CORD | CONTROL | PVC GRS | PVC 40 | PLC-AB/MCC-AB2/MCC-AB3 | P-VLT25 | DB-4 | SPARE |  |  | 68
E-36 | SP31-1101B | 2" | PULL CORD | CONTROL | PVC GRS | PVC 40 | P-VLT25 | JB-31-1000 |  | SPARE |  |  | 69
E-36 | SP31-2101A | 2" | PULL CORD | CONTROL | PVC GRS | PVC 40 | P-VLT25 | JB-31-2000 | DB-14 | SPARE |  |  | 68
E-38 | SP31-4101A | 2" | PULL CORD | CONTROL | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SPARE |  |  | 68
E-38 | SP31-4101B | 2" | PULL CORD | CONTROL | PVC GRS | PVC 40 | P-VLT26 | JB-31-4000 |  | SPARE |  |  | 69
E-39 | SP31-1110A | 3" | PULL CORD | SIGNAL | PVC GRS | PVC 40 | PLC-AB/MCC-AB2/MCC-AB3 | A-VLT25 | DB-4 | SPARE |  |  | 77
E-39 | SP31-1110B | 2" | PULL CORD | SIGNAL | PVC GRS | PVC 40 | A-VLT25 | JB-31-1001 |  | SPARE |  |  | 77
E-39 | SP31-2110 | 2" | PULL CORD | SIGNAL | PVC GRS | PVC 40 | A-VLT25 | JB-31-2001 | DB-14 | SPARE |  |  | 78
E-39 | SP31-4110A | 2" | PULL CORD | SIGNAL | PVC GRS | PVC 40 | A-VLT25 | A-VLT26 | DB-14 | SPARE |  |  | 78
E-39 | SP31-4100B | 2" | PULL CORD | SIGNAL | PVC GRS | PVC 40 | A-VLT26 | JB-31-4001 |  | SPARE |  |  | 79
E-36 | SP31-5300A | 1" | PULL CORD | 480VAC | PVC GRS | PVC 40 | MCC-AB2 | P-VLT25 | DB-4 | SPARE; STUB UP 6" AND CAP |  |  | 80
E-36 | SP31-5300B | 1" | PULL CORD | 480VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14 | SPARE; STUB UP 6" AND CAP |  |  | 81
E-36 | SP31-5300C | 1" | PULL CORD | 480VAC | PVC GRS | PVC 40 | P-VLT26 | 31-BLR-5300 | DB-15 | SPARE; STUB UP 6" AND CAP |  |  | 82
E-38 | SP31-5400A | 1" | PULL CORD | 120VAC | PVC GRS | PVC 40 | P-VLT26 | 31-BLR-5400 | DB-15 | SPARE; STUB UP 6" AND CAP |  |  | 83
E-41 | SP32-1100A | 1.5" | PULL CORD | 120VAC | PVC GRS | PVC 40 | DP-AB2 | P-VLT25 | DB-4
E-41 | SP32-1100B | 1.5" | PULL CORD | 120VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14
E-41 | SP32-1100C | 1.5" | PULL CORD | 120VAC | PVC GRS | PVC 40 | P-VLT26 | JB-32-1100 | DB-16
E-41 | SP32-1101 | 1.5" | PULL CORD | SIGNAL | PVC GRS | PVC 40 | A-VLT26 | JB-32-1101 | DB-16
E-41 | SP32-1200A | 1.5" | PULL CORD | 120VAC | PVC GRS | PVC 40 | DP-AB2 | P-VLT25 | DB-4
E-41 | SP32-1200B | 1.5" | PULL CORD | 120VAC | PVC GRS | PVC 40 | P-VLT25 | P-VLT26 | DB-14
E-41 | SP32-1200C | 1.5" | PULL CORD | 120VAC | PVC GRS | PVC 40 | P-VLT26 | JB-32-1100 | DB-16
E-41 | SP32-1200D | 1.5" | PULL CORD | 120VAC | PVC GRS | PVC 40 | JB-32-1100 | JB-32-1200 | DB-17
E-41 | SP32-1201A | 1.5" | PULL CORD | SIGNAL | PVC GRS | PVC 40 | A-VLT26 | JB-32-1101 | DB-16
E-41 | SP32-1201B | 1.5" | PULL CORD | SIGNAL | PVC GRS | PVC 40 | JB-32-1101 | JB-32-1201 | DB-17
E-42 | SP36-1000 | 1" | PULL CORD | SIGNAL | PVC GRS | PVC 40 | PLC-AB | V#20S | DB-33 | SPARE |  |  | 115
E-39 | SP36-1001 | 1" | PULL CORD | CONTROL | PVC GRS | PVC 40 | PLC-AB | V#20P | DB-33 | SPARE |  |  | 116
E-39 | SP36-1002 | 1" | PULL CORD | 120VAC | PVC GRS | PVC 40 | LP-AB | V#20P | DB-33 | SPARE |  |  | 117
E-42 | SP3-6 | 3" | 4 #14 | CONTROL | N/A | N/A | V#19P | V#20P | N/A | EXISTING CONDUIT USED FOR 51-G-1210 (START/STOP COMMAND) |  |  | 125
|  |  | 4 #14 | [6 empty] | EXISTING CONDUIT USED FOR 51-SG-1200 (START/STOP COMMAND)
|  | 3" | 4 #14 |  |  |  | V#20P | V#21P |  | EXISTING CONDUIT USED FOR 51-G-1210 (START/STOP COMMAND) |  |  | 126
|  |  | 4 #14 | [6 empty] | EXISTING CONDUIT USED FOR 51-SG-1200 (START/STOP COMMAND)
E-41 | SP51-2000A | 2-1" | PULL CORD | SIGNAL | PVC GRS | PVC 40 | A-VLT26 | A-VLT27 | DB-14 | SPARE |  |  | 127
E-40 | SP52-1000A | 1" | PULL CORD | CONTROL | PVC GRS | PVC 40 | MCC-AB1/MCC-AB4 | P-VLT28 | DB-6 | SPARE |  |  | 132
E-40 | SP52-1000B | 1" | PULL CORD | CONTROL | PVC GRS | PVC 40 | P-VLT28 | LCP-52-1001 | DB-9 | SPARE |  |  | 133
E-40 | SP52-1001A | 1" | PULL CORD | SIGNAL | PVC GRS | PVC 40 | PLC-AB | A-VLT28 | DB-6 | SPARE |  |  | 134
E-40 | SP52-1001B | 1" | PULL CORD | SIGNAL | PVC GRS | PVC 40 | A-VLT28 | LCP-52-1001 | DB-9 | SPARE |  |  | 135
E-40 | SP52-1100A | 2" | PULL CORD | 480VAC | PVC GRS | PVC 40 | MCC-AB1/MCC-AB4 | P-VLT28 | DB-6 | SPARE |  |  | 136
E-40 | SP52-1100B | 2" | PULL CORD | 480VAC | PVC GRS | PVC 40 | P-VLT28 | LCP-52-1001 | DB-9 | SPARE |  | 14-14-14 | 137
COMMUNICATION CONDUIT | [11 empty] | 15-15-15 | 151
SHEET | CONDUIT | SIZE | CONDUCTORS | SERVICE | AG MATERIAL | UG MATERIAL | FROM | TO | DUCTBANKS | NOTES |  |  | 152
E-42 | F001 | 2" | 24 - STRAND FIBER | COMM | PVC GRS | PVC 40 | CTC-AB | A-VLT25 | DB-4 |  |  |  | 153
E-42 | F002 | 2" | 24 - STRAND FIBER | COMM | PVC GRS | PVC 40 | A-VLT25 | A-VLT26 | DB-14 |  |  |  | 154
E-42 | F003 | 2" | 24 - STRAND FIBER | COMM | PVC GRS | PVC 40 | A-VLT26 | V#19S |  |  |  |  | 155
E-42 | F004 | 2" | 24 - STRAND FIBER | COMM | PVC GRS | PVC 40 | V#19S | CTC-AD | EXISTING | VIA V#13S -> V#12S -> CTC-AD |  |  | 156
E-41 | F010 | 2" | 24 - STRAND FIBER | COMM | PVC GRS | PVC 40 | CTC-AB | A-VLT25 | DB-4 |  |  |  | 157
E-41 | F011 | 2" | 24 - STRAND FIBER | COMM | PVC GRS | PVC 40 | A-VLT25 | A-VLT26 | DB-14 |  |  |  | 158
E-41 | F012 | 2" | 24 - STRAND FIBER | COMM | PVC GRS | PVC 40 | A-VLT26 | A-VLT27 | DB-15 |  |  |  | 159
E-41 | F013 | 2" | 24 - STRAND FIBER | COMM | PVC GRS | PVC 40 | A-VLT27 | CTC-RWDP | DB-18 |  |  |  | 160
E-41 | F014 | 2" | 24 - STRAND FIBER | COMM | PVC GRS | PVC 40 | CTC-RWDP | A-VLT28/CTC-MMWD | DB-19 |  |  |  | 160
E-40 | F015 | 2" | 24 - STRAND FIBER | COMM | PVC GRS | PVC 40 | CTC-AB | A-VLT28 | DB-6 |  |  |  | 160
E-40 | F016 | 2" | 24 - STRAND FIBER | COMM | PVC GRS | PVC 40 | A-VLT28 | CTC-RWTF | DB-9 | VIA LCP-52-1001 SPARE CONDUIT TO RWTF ELECTRICAL ROOM |  |  | 160
E-41 | F102 | 3/4" | 1 - CAT6 | COMM | PVC GRS | PVC 40 | PLC-AB | MCP-UV |  |  |  |  | 163
E-41 | F103 | 1" | 1 - CAT6 | COMM | PVC GRS | PVC 40 | PLC-MCC3 | LCP-62-ME-2100 | DB-25 |  |  |  | 163
E-41 | F104 | 1" | 4 - CAT6 | COMM | PVC GRS | PVC 40 | RWDP VFDS | CTC-RWDP |  |  |  |  | 163
|  |  | LOT CAT6 | COMM |  |  | MCC-AB1/MCC-AB2/MCC-AB3/MCC-AB4 | CTC-AB |  | CAT6 CABLES AS NEEDED

## Ductbank Schedule
DUCTBANK | CONDUIT | SERVICE | FROM | TO | CONDUITS | NOTES
DB-1 | 8-4" | 480VAC | NEW TRANSFORMER | MAIN SES | P001A
DB-2 | 8-4" | 480VAC | MAIN SES | MAIN ATS | P001B
DB-3 | 6-3" | 480VAC | NEW GENERATOR | MAIN ATS | P002A
| 1" | 120VAC | NEW GENERATOR | EB TRENCH | P002C
| 1" | CONTROL | NEW GENERATOR | EB TRENCH | C002B
| 1" | SIGNAL | NEW GENERATOR | EB TRENCH | S002A
DB-4 | 1" | 480VAC | DP-AB2 | P-VLT25 | P051
| 1" |  | SWBD-AB1 |  | P112A
| 1" |  | SWBD-AB1 |  | P121
| 1" |  | MCC-AB1 |  | P23-1100A
| 1" |  | MCC-AB1 |  | P23-1200A
| 1" |  | MCC-AB4 |  | P23-1300A
| 1" |  | MCC-AB1 |  | P23-1400A
| 1" |  | MCC-AB4 |  | P23-1500A
| 1" |  | MCC-AB2 |  | P31-1100A
| 1" |  | MCC-AB2 |  | P31-1200A
| 1" |  | MCC-AB2 |  | P31-1300A
| 1" |  | MCC-AB2 |  | P31-1400A
| 1" |  | MCC-AB2 |  | P31-2100A
| 1" |  | MCC-AB2 |  | P31-2200A
| 1" |  | MCC-AB2 |  | P31-2300A
| 1" |  | MCC-AB2 |  | P31-2400A
| 1" |  | MCC-AB3 |  | P31-3100A
| 1" |  | MCC-AB3 |  | P31-3200A
| 1" |  | MCC-AB3 |  | P31-3300A
| 1" |  | MCC-AB3 |  | P31-3400A
| 1" |  | MCC-AB3 |  | P31-4100A
| 1" |  | MCC-AB3 |  | P31-4200A
| 1" |  | MCC-AB3 |  | P31-4300A
| 1" |  | MCC-AB3 |  | P31-4400A
| 2" |  | DP-AB2 |  | P31-3540A
| 2" |  | DP-AB2 |  | P31-4550A
| 1" |  | MCC-AB2 |  | P31-5300A
| 1" |  | MCC-AB3 |  | P31-5400A
| 1" |  | MCC-AB3 |  | P32-1100A
| 1" |  | MCC-AB2 |  | P32-1200A
| 1" |  | MCC-AB3 |  | P32-1300A
| 2" |  | DP-AB2 |  | P33-1100A
| 1" |  | MCC-AB2 |  | P36-1100A
| 1" |  | MCC-AB2 |  | P36-1200A
| 1" |  | MCC-AB3 |  | P36-1300A
| 1" |  | DP-AB2 |  | P36-1400A
| 4-4" |  | SWBD-AB1 |  | P51A
| 1" |  | MCC-AB2 |  | P61-1100A
| 1" |  | MCC-AB3 |  | P61-1200A
| 1" |  | MCC-AB2 |  | P61-1300A
| 1" |  | DP-AB2 |  | SP23-1000A
| 1" |  | MCC-AB |  | SP23-1000C
| 2" |  | MCC-AB |  | SP31-1100A
| 2" |  | MCC-AB |  | SP31-2100A
| 2" |  | MCC-AB |  | SP31-4100A
| 1" |  | MCC-AB |  | SP31-5300A
| 1.25" | 120VAC | LP-AB |  | P23-1000A
| 1" |  | LP-AB |  | SP23-1000B
| 2" |  | LP-AB |  | P31-1001A
| 2" |  | LP-AB |  | P31-2001A
| 1" |  | LP-AB |  | P31-5500A
| 1" |  | LP-AB |  | P32-1101A
| 1" |  | LP-AB |  | P36-1000A
| 1" |  | LP-AB |  | SP31-1000A
| 1" |  | LP-AB |  | SP31-2000A
| 1" |  | LP-AB |  | SP31-4000A
| 1.5" |  | DP-AB2 |  | SP32-1100A
| 1.5" |  | DP-AB2 |  | SP32-1200A
| 1" | CONTROL | MCC-AB1 |  | C23-1100A
| 1" |  | MCC-AB4 |  | C23-1200A
| 1" |  | MCC-AB1 |  | C23-1300A
| 1" |  | MCC-AB1 |  | C23-1400A
| 1" |  | MCC-AB4 |  | C23-1500A
| 2" |  | MCC-AB2 |  | C31-1100A
| 2" |  | MCC-AB2 |  | C31-2100A
| 2" |  | MCC_AB3 |  | C31-3100A
| 2" |  | MCC-AB3 |  | C31-4100A
| 1" |  | MCC-AB2 |  | C31-5300A
| 1.5" |  | MCC-AB2/MCC-AB3 |  | C32-1100A
| 1.5" |  | PLC-AB |  | C36-1400A
| 1" |  | MCC-AB2 |  | C61-1100A
| 1" |  | MCC-AB3 |  | C61-1200A
| 1" |  | MCC-AB2 |  | C61-1300A
| 2" |  | PLC-AB/MCC-AB2/MCC-AB3 |  | SP31-1101A
| 1.5 | SIGNAL | PLC-AB | A-VLT25 | S121A
| 3" |  | PLC-AB |  | S23-1000A
| 2" |  | MCC-AB1/MCC-AB4 |  | S23-1100A
| 2" |  | MCC-AB2/MCC-AB3 |  | C31-1100E
| 3" |  | PLC-AB/MCC-AB1/MCC-AB4 |  | S31-1100A
| 1" |  | PLC-AB |  | S31-5510A
| 2" |  | PLC-AB |  | SP31-1110A
| 2" | COMM | CTC-AB |  | F001
| 2" |  | CTC-AB |  | F010
DUCTBANK | CONDUIT | SERVICE | FROM | TO | CONDUITS | NOTES
DB-5 | 2" | 480VAC | DP-AB2 | LP-UV-2 TXFR | P108A
| 2" |  | DP-AB2 | DS-PSU-UV-1 | P105A
| 2" |  | DP-AB2 | DS-PSU-UV-2 | P106A
| 1" |  | MCC-AB2 | DS-44-H-1100 | P44-1100A
| 1" |  | DP-AB2 | DS-44-G-1310 | P44-1310A
| 1" |  | DP-AB2 | DS-44-G-1320 | P44-1320A
| 1" |  | DP-AB2 | DS-44-G-1330 | P44-1330A
| 1" |  | DP-AB2 | DS-44-G-1340 | P44-1340A
| 1" |  | DP-AB2 | DS-44-G-1350 | P44-1350A
| 1" |  | MCC-AB2 | DS-44-H-1510 | P44-1510A
| 1" |  | MCC-AB3 | DS-44-H-1520 | P44-1520A
| 1" | 120VAC | PLC-AB | 44-H-1611 | P44-1611
| 1" |  | PLC-AB | 44-H-1621 | P44-1621
| 1" |  | PLC-AB | 44-H-1621 | P44-1621
| 1" |  | PLC-AB | LP-UV-2 TXFR | P110
| 1" | CONTROL | PLC-AB | 44-G-1310 | C44-1310
| 1" |  | PLC-AB | 44-G-1320 | C44-1320
| 1" |  | PLC-AB | 44-G-1330 | C44-1330
| 1" |  | PLC-AB | 44-G-1340 | C44-1340
| 1" |  | PLC-AB | 44-G-1350 | C44-1350
| 1" | SIGNAL | PLC-AB | 44-FSH-1500 | S44-1500
| 1" |  | PLC-AB | 44-G-1310 | S44-1310
| 1" |  | PLC-AB | 44-G-1320 | S44-1320
| 1" |  | PLC-AB | 44-G-1330 | S44-1330
| 1" |  | PLC-AB | 44-G-1340 | S44-1340
| 1" |  | PLC-AB | 44-G-1350 | S44-1350
| 1" |  | PLC-AB | 44-TT-1530/44-AE-1530 | S44-1530
| 1" |  | PLC-AB | 44-TT-1550/44-AE-1550 | S44-1550
| 1" |  | PLC-AB | HVAC INSTRUMENTATION | S44-1900
DB-6 | 1" | 480VAC | MCC-AB2 | P-VLT28 | P23-2100A
| 1" |  | MCC-AB3 |  | P23-2200A
| 1" |  | MCC-AB3 |  | P23-2300A
| 2" |  | VFD-52-P-1013 |  | P52-1013B
| 2" |  | VFD-52-P-1014 |  | P52-1014B
| 2" |  | MCC-AB |  | SP52-1100A
| 1" | 120VAC | LP-AB |  | P066
| 1.5" |  | LP-AB |  | P43-1000A
| 1" |  | LP-AB |  | P43-1100A
| 1" |  | LP-AB |  | P43-1200A
| 2" |  | LP-AB |  | P43-1400A
| 1" |  | LP-AB |  | P43-H1520A
| 2" | CONTROL | VFD-52-P-1013/VFD-52-P-1014 |  | C52-1013A
| 1" |  | MCC-AB |  | SP52-1000A
| 1" | SIGNAL | PLC-AB | A-VLT28 | S23-1020C
| 1.5" |  | PLC-AB |  | S43-1000A
| 1" |  | VFD-52-P-1013 |  | S52-1013A
| 1" |  | VFD-52-P-1014 |  | S52-1014
| 2" |  | CTC-AB |  | F015
| 1" |  | PLC-AB |  | SP52-1001A
DB-7 | 1.5" | 120VAC | P-VLT28 | FUEL TANK CONTROLLER | P067
| 1" |  |  | JB-43-1000 | P43-1000B
| 1" |  |  | JB-43-1000 | P43-1100B
| 1" |  |  | JB-43-1000 | P43-1200B
| 2" |  |  | JB-43-1000 | P43-1400B
| 1" |  |  | JB-43-1000 | P43-H1520B
| 1.5" | SIGNAL | A-VLT28 | JB-43-1001 | S43-1000B
DB-9 | 1" | 480VAC | P-VLT28 | JB-23-2000 | P23-2100B
| 1" |  |  | JB-23-2000 | P23-2200B
| 1" |  |  | JB-23-2000 | P23-2300B
| 2" |  |  | 52-P-1013 | P52-1013C
| 2" |  |  | 52-P-1013 | P52-1014C
| 1' |  |  | JB-23-1000 | SP066
| 2" |  |  | LCP-52-1001 | SP52-1100B
| 2" | CONTROL |  | LCP-52-1001 | C52-1013B
| 1" |  |  | JB-23-2000 | SP067
| 1" |  |  | LCP-52-1001 | SP52-1000B
| 1" | SIGNAL | A-VLT28 | JB-23-2001 | S23-1020D
| 1" |  |  | LCP-52-1001 | S52-1013B
| 2" |  |  | LCP-52-1001 | F016
| 1" |  |  | JB-23-2001 | SP068
| 1" |  |  | LCP-52-1001 | SP52-1001B
DB-10 | 2" | 480VAC | MCC-3 | P-VLT1 | P21-1200A
| 2" |  | DP-MCC3 |  | P21-1210A
| 2" |  | MCC-3 |  | P21-1300A
| 2" |  | DP-MCC-3 |  | P22-2201A
| 2" | 120VAC | LP-MCC3 |  | P21-1204A
| 2" |  | LP-MCC3 |  | P22-1204A
| 2" | SIGNAL | PLC-MCC3 | A-VLT1 | S21-1210A
| 2" |  | PLC-MCC3 |  | S22-2201A
DUCTBANK | CONDUIT | SERVICE | FROM | TO | CONDUITS | NOTES
DB-14 | 1" | 480VAC | P-VLT25 | P-VLT26 | P052
| 1" |  |  |  | P112B
| 1" |  |  |  | P23-1100B
| 1" |  |  |  | P23-1200B
| 1" |  |  |  | P23-1300B
| 1" |  |  |  | P23-1400B
| 1" |  |  |  | P23-1500B
| 1" |  |  | JB-31-2000 | P31-2100B
| 1" |  |  |  | P31-2200B
| 1" |  |  |  | P31-2300B
| 1" |  |  |  | P31-2400B
| 1" |  |  |  | P31-3100B
| 1" |  |  |  | P31-3200B
| 1" |  |  |  | P31-3300B
| 1" |  |  |  | P31-3400B
| 1" |  |  | P-VLT26 | P31-4100B
| 1" |  |  |  | P31-4200B
| 1" |  |  |  | P31-4300B
| 1" |  |  |  | P31-4400B
| 2" |  |  | JB-31-2000 | P31-3540B
| 2" |  |  | P-VLT26 | P31-4550B
| 1" |  |  |  | P31-5300B
| 1" |  |  |  | P31-5400B
| 1" |  |  |  | P32-1100B
| 1" |  |  |  | P32-1200B
| 1" |  |  |  | P32-1300B
| 2" |  |  |  | P33-1100B
| 1" |  |  |  | P36-1100B
| 1" |  |  |  | P36-1200B
| 1" |  |  |  | P36-1300B
| 1" |  |  |  | P36-1400B
| 4-4" |  |  |  | P51B
| 1" |  |  |  | P61-1100B
| 1" |  |  |  | P61-1200B
| 1" |  |  |  | P61-1300B
| 1" |  |  |  | SP23-1000E
| 1" |  |  |  | SP23-1000G
| 2" |  |  | JB-31-2000 | SP31-2100B
| 2" |  |  |  | SP31-4100B
| 1" |  |  | P-VLT26 | SP31-5300B
| 1" | 120VAC |  |  | P23-1000B
| 1" |  |  |  | P31-2000A
| 1" |  |  | JB-31-2000 | P31-5500B
| 1" |  |  | P-VLT26 | P32-1101B
| 1" |  |  |  | P36-1000B
| 1" |  |  | JB-31-2000 | SP31-2000B
| 1" |  |  | P-VLT26 | SP23-1000F
| 1" |  |  |  | SP31-4000B
| 1.5" |  |  |  | SP32-1100B
| 1.5" |  |  |  | SP32-1200B
| 1" | CONTROL |  |  | C23-1100B
| 1" |  |  |  | C23-1200B
| 1" |  |  |  | C23-1300B
| 1" |  |  |  | C23-1400B
| 1" |  |  |  | C23-1500B
| 2" |  |  | JB-31-2000 | C31-2100B
| 2" |  |  |  | C31-3100B
| 2" |  |  | P-VLT26 | C31-4100B
| 1" |  |  |  | C31-4100F
| 1" |  |  |  | C31-5300B
| 1.5" |  |  |  | C32-1100B
| 1.5" |  |  |  | C36-1400B
| 1" |  |  |  | C61-1100B
| 1" |  |  |  | C61-1200B
| 1" |  |  |  | C61-1300B
| 2" |  |  | JB-23-2001 | SP31-2101A
| 2" |  |  | P-VLT26 | SP31-4101A
| 3" | SIGNAL | A-VLT25 | JB-23-2001 | S31-2001A
| 1.5 |  |  | A-VLT26 | S121B
| 2" |  |  |  | S23-1000B
| 2" |  |  |  | S23-1100B
| 2" |  |  |  | S31-4100A
| 1" |  |  | JB-31-2001 | S31-5510B
| 1" |  |  | A-VLT26 | SP23-1000H
| 2" |  |  | JB-31-2001 | SP31-2110
| 2" |  |  | A-VLT26 | SP31-4110A
| 2" | COMM |  |  | F002
| 2" |  |  |  | F011
DUCTBANK | CONDUIT | SERVICE | FROM | TO | CONDUITS | NOTES
DB-15 | 1" | 480VAC | P-VLT26 | P-VLT27 | P051C
| 1" |  |  | DS-23-P-1100 | P23-1100C
| 1" |  |  | DS-23-P-2100 | P23-1200C
| 1" |  |  | DS-23-P-3100 | P23-1300C
| 1" |  |  | DS-23-P-4100 | P23-1400C
| 1" |  |  | DS-23-P-5100 | P23-1500C
| 1" |  |  | DS-31-BLR-5300 | P31-5300C
| 1" |  |  | DS-31-BLR-5400 | P31-5400C
| 1" |  |  |  | P32-1300C
| 2" |  |  |  | P33-1100C
| 1" |  |  |  | P36-1100C
| 1" |  |  |  | P36-1200C
| 1" |  |  |  | P36-1300C
| 1" |  |  |  | P36-1400C
| 4-4" |  |  |  | P51C
| 1" |  |  | DS-61-P-1100 | P61-1100C
| 1" |  |  | DS-61-P-1200 | P61-1200C
| 1" |  |  | DS-61-P-1300 | P61-1300C
| 1" | 120VAC |  | JB-23-1000 | P23-1000C
| 1" |  |  | P-VLT27 | P36-1000C
| 1" | CONTROL |  | LCP-23-P-1100 | C23-1100C
| 1" |  |  | LCP-23-P-1200 | C23-1200C
| 1" |  |  | LCP-23-P-1300 | C23-1300C
| 1" |  |  | LCP-23-P-1400 | C23-1400C
| 1" |  |  | LCP-23-P-1500 | C23-1500C
| 1" |  |  | DS-31-BLR-5300 | C31-5300C
| 1.5" |  |  | P-VLT27 | C36-1100A
| 1.5" |  |  | P-VLT27 | C36-1400C
| 1" |  |  | LCP-61-P-1100 | C61-1100C
| 1" |  |  | LCP-61-P-1200 | C61-1200C
| 1" |  |  | LCP-61-P-1300 | C61-1300C
| 3" | SIGNAL | A-VLT26 | JB-23-2001 | S31-2001A
| 1.5 |  |  | A-VLT27 | S121C
| 1" |  |  | LCP-23-P-1100 | S23-1100C
| 1" |  |  | LCP-23-P-1200 | S23-1200
| 1" |  |  | LCP-23-P-1300 | S23-1300
| 1" |  |  | LCP-23-P-1400 | S23-1400
| 1" |  |  | LCP-23-P-1500 | S23-1500
| 1" |  |  | 31-PIT-5000 | S31-5000
| 1" |  |  | A-VLT27 | S36-1000A
| 1" |  |  | JB-31-2001 | S31-5510C
| 2" |  |  | A-VLT27 | S51-1000A
| 1" |  |  | 31-BLR-5300 | SP31-5300C
| 2" |  |  | 31-BLR-5400 | SP31-5400C
| 2 - 1" |  |  | A-VLT27 | SP51-2000A
| 2" | COMM |  | A-VLT27 | F012
DUCTBANK | CONDUIT | SERVICE | FROM | TO | CONDUITS | NOTES
DB-16 | 1" | 480VAC | P-VLT26 | JB-32-1100 | P32-1101C
| 1" |  |  |  | P32-1100C
| 1" |  |  |  | P32-1200C
| 1.5" | 120VAC |  |  | SP32-1100C
| 1.5" |  |  |  | SP32-1200C
| 1" | CONTROL |  |  | C32-1100C
| 1.5" | SIGNAL | A-VLT26 |  | SP32-1101
| 1.5" | SIGNAL |  |  | SP32-1201A
DB-17 | 1" | 480VAC | JB-32-1100 | JB-32-1200 | P32-1200D
| 1" | 120VAC |  |  | P32-1201
| 1.5" |  |  |  | SP32-1200D
| 1" | CONTROL |  |  | C32-1200A
| 1.5" | SIGNAL |  |  | SP32-1201B
DB-18 | 4-4" | 480VAC | P-VLT27 | DP-RWDP | P51D
| 1" | CONTROL |  | JB-51-2000 | C51-2100A
| 1.5 | SIGNAL | A-VLT27 | A-VLT30 | S121D
| 2" |  |  | JB-51-2001 | S51-1000B
| 2" | COMM |  | CTC-RWDP | F013
DB-19 | 2" | 120VAC | LP-RWDP | P-VLT30 | P120
| 2" |  |  |  | P121
| 1" |  |  |  | P122
| 1" |  |  |  | P123
| 2" | SIGNAL | A-VLT27 | A-VLT30 | F014
| 1.5 | SIGNAL | A-VLT27 | A-VLT30 | S121D
DB-21 | 1" | 120VAC | V#20P | POND RETURN METER VAULT | P44-1000
| 1" | 120VAC | V#20P | SECONDARY EFFLUENT VAULT | P51-1009C
| 1" | SIGNAL | V#20S | 42-FE-1120 | S42-1120C
| 1" |  |  | 42-LSH-1120 | S42-1120C
| 1" |  |  | 44-FE-1000 | S44-1000C
| 1" |  |  | 44-LSH-1000 | S42-1120D
| 1" |  |  | 51-FE-1009 | S51-1009C
| 1" |  |  | 51-LSH-1009 | S51-1000D
DB-25 | 4-4" | 480VAC | MCC-3 | LCP-62-ME-2100 | P62-2100
| 1" | 120VAC | LP-MCC3 | SITE LIGHTS | P71
| 1" |  |  | 62-FIT-2620 | P62-2620
| 1" |  |  | 62-FIT-2640 | P62-2640
| 2" | COMM | PLC-MCC3 | LCP-62-ME-2100 | F103
DB-30 | 1" | 480VAC | P-VLT26 | V#19P | P053
| 1" |  |  |  | P112C
DB-33 | 1" | 480VAC | DP-AB2 | V#20P | P41-1000
| 1" | 120VAC | LP-AB |  | P41-1100
| 1" |  |  |  | P44-1000A
| 1" |  |  |  | SP36-1002
| 2" | SIGNAL | 42-FIT-1110 | V#20S | S42-1120B
| 2" | SIGNAL | 44-FIT-1000 |  | S44-1000B
| 2" | SIGNAL | 51-FIT-1009 |  | S51-1009B
| 1" | SIGNAL | PLC-AB |  | SP36-1001
| 1" | SIGNAL |  |  | SP36-1000
| 1" | SIGNAL |  |  | S41-1100A
DB-36 | 1" | 480VAC | P-VLT27 | DS-36-P-1100 | P36-1100D
| 1" |  |  | DS-36-P-1200 | P36-1200D
| 1" |  |  | DS-36-P-1300 | P36-1300D
| 1" |  |  | DS-36-V-1400 | P36-1400D
| 1" |  |  | DS-36-V-1410 | P36-1410A
| 1" | 120VAC |  | LIGHTING | P36-1000D
| 1" | CONTROL |  | LCP-36-P-1100 | C36-1100B
| 1" |  |  | LCP-36-P-1200 | C36-1200A
| 1" |  |  | LCP-36-P-1300 | C36-1300A
| 1" |  |  | 36-V-1400 | C36-1400D
| 1" |  |  | 36-V-1410 | C36-1410
| 1" | SIGNAL | A-VLT27 | 36-FIT-1000 | S36-1000B
| 1" |  |  | 36-V-1400 | S36-1400
| 2" |  |  | 36-V-1410 | S36-1410